{"text_format":"1","workbook":"xlsx","n_sheets":5,"sheets":["Gegevens invoeren","Berekeningen","Database","Weersgegevens","Subsidie"],"not_rendered":{"charts":1,"images":1,"macros":1,"external_links":0,"defined_names":37,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Gegevens invoeren","index":0,"n_rows":34,"n_cols":12,"rows_kept":34,"cut":false,"hidden":false,"merged":[]}
["Gegevens invullen:",null,null,null,null,"Berekende waarden:"]
["Tankgegevens","Du",45,"m",null,"Warmtelek door","bodem",{"$f":"(Berekeningen!C28*Berekeningen!J9)/1000","v":63.195944935622492},"kW",null,"Inschattting stoomkosten over de opslagperiode:"]
[null,"Ti",50,"C",null,null,"natte wand",{"$f":"(Berekeningen!D28*Berekeningen!J11)/1000","v":32.437324366546889},"kW",null,null,{"$f":"(H6*24*Berekeningen!N14*3.6/Berekeningen!I16)/0.85*C23","v":40299.816517815954}]
[null,"h",15,"m",null,null,"droge wand",{"$f":"(Berekeningen!F28*Berekeningen!J12)/1000","v":1.2936240272206507},"kW"]
[null,"vulling",95,"%",null,null,"dak",{"$f":"(Berekeningen!E28*Berekeningen!J10)/1000","v":13.599482172160616},"kW"]
["wand","isolatiemateriaal","steen- of glaswol",null,null,null,"totaal",{"$f":"SUM(H2:H5)","v":110.52637550155065},"kW"]
[null,"dikte isolatie",0.1,"m"]
[null,"kleur wand","aluminium",null,null,null,"<--gebruik bij voorkeur de linkerknop"]
["dak","isolatiemateriaal","PIR",null,null,null,"de rechter is voor als de linker niet werkt."]
[null,"dikte isolatie",0.1,"m",null,null,"Wel elke keer op OK klikken na elke sol-"]
[null,"dikte afdekmateriaal",0,"m",null,null,"verstap!"]
[null,"kleur dak","witte verf",null,null,"Resultaat:"]
[null,"vorm dak","conisch",null,null,{"$f":"IF(SUM(Berekeningen!D30:F30)<0.001,\"Berekening succesvol uitgevoerd\",\"Berekening mislukt, probeer nogmaals of probeer de tweede knop\")","v":"Berekening succesvol uitgevoerd"}]
["bodem (tot 1 m diep)","zand",0.85,"m"]
[null,"klei",0.15,"m"]
[null,"beton",0,"m"]
[null,"foamglas",0,"m"]
[null,"zandbitumen",0,"m"]
["opslagperiode","van","2013-01-01"]
[null,"tot en met","2013-12-31"]
["weersgegevens","weerstation","Rotterdam"]
["stoomgegevens","druk",8,"barg"]
[null,"prijs",20,"€/ton"]
["aannames","dikte staal",0.01,"m"]
[null,"bodemtemperatuur",12.5,"C"]
[]
[]
["Opgezochte waarden:"]
["u",{"$f":"Berekeningen!L7","v":4.3589389799635709},"gemiddelde over 15 jaren"]
["Tu",{"$f":"Berekeningen!L6","v":10.793155737704909},"gemiddelde over 15 jaren"]
["k isolatie wand",{"$f":"VLOOKUP(C6,k_waarden,2,FALSE)+C31","v":4.3000000000000003E-2},{"$f":"IF(C6=\"PIR\",(C3-10)/10*0.0007,IF(C6=\"PUR\",(C3-10)/10*0.0007,(C3-10)/10*0.002))","v":8.0000000000000002E-3},"(correctie)"]
["k isolatie dak",{"$f":"VLOOKUP(C9,k_waarden,2,FALSE)+C32","v":2.58E-2},{"$f":"IF(C9=\"PIR\",(C3-10)/10*0.0007,IF(C9=\"PUR\",(C3-10)/10*0.0007,(C3-10)/10*0.002))","v":2.8E-3},"(correctie)"]
["emissiefactor wand",{"$f":"VLOOKUP(C8,emissiefactor,2,FALSE)","v":0.33}]
["emissiefactor dak",{"$f":"VLOOKUP(C12,emissiefactor,2,FALSE)","v":0.9}]

{"sheet":"Berekeningen","index":1,"n_rows":30,"n_cols":17,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
["Berekeningen",null,null,null,null,null,null,"Andere hulpwaarden"]
[null,null,"Bodem","Natte wand","Dak","Droge wand",null,"datum",{"$f":"MONTH('Gegevens invoeren'!C19)","v":1},{"$f":"DAY('Gegevens invoeren'!C19)","v":1},{"$f":"IF(LEN(I2)=1,CONCATENATE(0,I2),I2)","v":"01"},{"$f":"IF(LEN(J2)=1,CONCATENATE(0,J2),J2)","v":"01"},{"$f":"CONCATENATE('Gegevens invoeren'!C21,K2,L2)","v":"Rotterdam0101"},"langer dan een jaar?",null,{"$f":"IF(DAYS360('Gegevens invoeren'!C19,'Gegevens invoeren'!C20)>360,\"ja\",\"nee\")","v":"nee"},{"$f":"ROUNDDOWN(DAYS360('Gegevens invoeren'!C19,'Gegevens invoeren'!C20)/360,0)","v":1}]
["Afhankelijke waarden","vouw in",null,null,{"$f":"HLOOKUP(ROUND(E13,-1),nweluchtinfo,5,FALSE)","v":1.8335E-5},null,null,null,{"$f":"MONTH('Gegevens invoeren'!C20)","v":12},{"$f":"DAY('Gegevens invoeren'!C20)","v":31},{"$f":"IF(LEN(I3)=1,CONCATENATE(0,I3),I3)","v":12},{"$f":"IF(LEN(J3)=1,CONCATENATE(0,J3),J3)","v":31},{"$f":"CONCATENATE('Gegevens invoeren'!C21,K3,L3)","v":"Rotterdam1231"},"jaaroverschrijdend?",null,{"$f":"IF(YEAR('Gegevens invoeren'!C20)>YEAR('Gegevens invoeren'!C19),\"ja\",\"nee\")","v":"nee"}]
[null,"vouw uit",null,{"$f":"HLOOKUP(ROUND(D25,-1),nweluchtinfo,5,FALSE)","v":1.4535000000000001E-5},{"$f":"HLOOKUP(ROUND(E25,-1),nweluchtinfo,5,FALSE)","v":1.4535000000000001E-5},{"$f":"HLOOKUP(ROUND(F25,-1),nweluchtinfo,5,FALSE)","v":1.4535000000000001E-5}]
[null,"Pr in",null,null,{"$f":"HLOOKUP(ROUND(E13,-1),nweluchtinfo,4,FALSE)","v":0.7310051016850222},null,null,null,null,null,null,"rekenwaarde","<j","<j jaaroverschrijdend",">j","jaargem"]
[null,"Pr uit",null,{"$f":"HLOOKUP(ROUND(D25,-1),nweluchtinfo,4,FALSE)","v":0.74367313104333566},{"$f":"HLOOKUP(ROUND(E25,-1),nweluchtinfo,4,FALSE)","v":0.74367313104333566},{"$f":"HLOOKUP(ROUND(F25,-1),nweluchtinfo,4,FALSE)","v":0.74367313104333566},null,"weer",null,null,"gemiddelde temp",{"$f":"IF(P2=\"ja\",O6,IF(P3=\"ja\",N6,M6))","v":10.793155737704909},{"$f":"AVERAGEIFS(temperatuur,key,\">=\"&M2,key,\"<=\"&M3)","v":10.793155737704909},{"$f":"N10/N12*AVERAGEIFS(temperatuur,key,\">=\"&M2,key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")+N11/N12*AVERAGEIFS(temperatuur,key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&M3)","v":7.2019963536918814},{"$f":"N10/N12*AVERAGEIFS(temperatuur,key,\">=\"&M2,key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")+N11/N12*AVERAGEIFS(temperatuur,key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&M3)+Q2*365/N12*P6","v":10.793155737704909},{"$f":"AVERAGEIFS(temperatuur,key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")","v":10.793155737704909}]
[null,"k in",null,null,{"$f":"HLOOKUP(ROUND(E13,-1),nweluchtinfo,6,FALSE)","v":2.7920999999999998E-2},null,null,null,null,null,"gemiddelde wind",{"$f":"IF(P2=\"ja\",O7,IF(P3=\"ja\",N7,M7))","v":4.3589389799635709},{"$f":"AVERAGEIFS(wind,key,\">=\"&M2,key,\"<=\"&M3)","v":4.3589389799635709},{"$f":"N10/N12*AVERAGEIFS(wind,key,\">=\"&M2,key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")+N11/N12*AVERAGEIFS(wind,key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&M3)","v":2.9086083257368585},{"$f":"N10/N12*AVERAGEIFS(wind,key,\">=\"&M2,key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")+N11/N12*AVERAGEIFS(wind,key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&M3)+Q2*365/N12*P7","v":4.3589389799635709},{"$f":"AVERAGEIFS(wind,key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")","v":4.3589389799635709}]
[null,"k uit",null,{"$f":"HLOOKUP(ROUND(D25,-1),nweluchtinfo,6,FALSE)","v":2.4840999999999998E-2},{"$f":"HLOOKUP(ROUND(E25,-1),nweluchtinfo,6,FALSE)","v":2.4840999999999998E-2},{"$f":"HLOOKUP(ROUND(F25,-1),nweluchtinfo,6,FALSE)","v":2.4840999999999998E-2}]
["Berekende waarden","Lc",null,null,{"$f":"(1-'Gegevens invoeren'!C5/100)*'Gegevens invoeren'!C4","v":0.75000000000000067},null,null,"oppervlakten","bodem",{"$f":"0.25*PI()*'Gegevens invoeren'!C2^2","v":1590.4312808798327},"m2",null,"weegfactoren weer"]
[null,"beta",null,null,{"$f":"1/(273+E13)","v":3.1271083427457571E-3},null,null,null,"dak",{"$f":"VLOOKUP('Gegevens invoeren'!C13,dak,2,FALSE)*J9","v":1646.0963757106267},"m2",null,"deel 1",{"$f":"COUNTIFS(key,\">=\"&M2,key,\"<=\"&'Gegevens invoeren'!C21&\"1231\")","v":366}]
[null,"Rtotaal",{"$f":"'Gegevens invoeren'!C14/VLOOKUP('Gegevens invoeren'!B14,k_waarden,2,FALSE)+'Gegevens invoeren'!C15/VLOOKUP('Gegevens invoeren'!B15,k_waarden,2,FALSE)+'Gegevens invoeren'!C16/VLOOKUP('Gegevens invoeren'!B16,k_waarden,2,FALSE)+'Gegevens invoeren'!C17/VLOOKUP('Gegevens invoeren'!B17,k_waarden,2,FALSE)+'Gegevens invoeren'!C18/VLOOKUP('Gegevens invoeren'!B18,k_waarden,2,FALSE)","v":0.94374999999999998},{"$f":"'Gegevens invoeren'!C7/'Gegevens invoeren'!B31+'Gegevens invoeren'!C24/Database!I13","v":2.3257813953488373},{"$f":"'Gegevens invoeren'!C24/Database!I13+'Gegevens invoeren'!C10/'Gegevens invoeren'!B32","v":3.8761689922480622},{"$f":"'Gegevens invoeren'!C7/'Gegevens invoeren'!B31+'Gegevens invoeren'!C24/Database!I13","v":2.3257813953488373},null,null,"natte wand",{"$f":"PI()*'Gegevens invoeren'!C2*'Gegevens invoeren'!C4*'Gegevens invoeren'!C5/100","v":2014.546289114455},"m2",null,"deel 2",{"$f":"COUNTIFS(key,\">=\"&'Gegevens invoeren'!C21&\"0101\",key,\"<=\"&M3)","v":366}]
[null,"Rcyl",null,null,null,null,null,null,"droge wand",{"$f":"PI()*'Gegevens invoeren'!C2*'Gegevens invoeren'!C4*(1-'Gegevens invoeren'!C5/100)","v":106.02875205865563},"m2",null,"totaal aant dagen",{"$f":"SUM(N10:N11)+Q2*365","v":1097}]
["Vrije convectie","Td",null,null,{"$f":"AVERAGE('Gegevens invoeren'!C3,E21)","v":46.784251261966219}]
[null,"Ra",null,null,{"$f":"E5*9.81*E10*('Gegevens invoeren'!C3-E21)*E9^3/E3^2","v":180994929.56735358},null,null,"starttemperatuur",{"$f":"(D21-'Gegevens invoeren'!B30)/2","v":19.603422131147546},null,null,null,"echt aantal dagen",{"$f":"'Gegevens invoeren'!C20-'Gegevens invoeren'!C19","v":364}]
[null,"Nu",null,null,{"$f":"0.061*E14^(1/3)","v":34.505260027824676}]
[null,"h in",null,null,{"$f":"E15*E7/E9","v":1.2845618203158558},{"$f":"E16","v":1.2845618203158558},null,"stoomgegevens",{"$f":"VLOOKUP(('Gegevens invoeren'!C22+1),stoomgegevens,4,TRUE)","v":2029.5},"kJ/kg","verdampingswarmte"]
["Gedwongen convectie","Re",null,{"$f":"'Gegevens invoeren'!B29*'Gegevens invoeren'!C2/D4","v":13495167.120630249},{"$f":"'Gegevens invoeren'!B29*E20/E4","v":10599079.47128463},{"$f":"'Gegevens invoeren'!B29*'Gegevens invoeren'!C2/F4","v":13495167.120630249}]
[null,"Nu",null,{"$f":"0.3+0.62*D17^0.5*D6^(1/3)/(1+(0.4/D6)^(2/3))^0.25*(1+(D17/282000)^(5/8))^(4/5)","v":13462.639684157279},{"$f":"(0.037*E17^0.8-871)*E6^(1/3)","v":13192.048412676026},{"$f":"0.3+0.62*F17^0.5*F6^(1/3)/(1+(0.4/F6)^(2/3))^0.25*(1+(F17/282000)^(5/8))^(4/5)","v":13462.639684157279}]
[null,"h uit",null,{"$f":"D18*D8/'Gegevens invoeren'!C2","v":7.431676275425577},{"$f":"E18*E8/E20","v":9.2721172773399676},{"$f":"F18*F8/'Gegevens invoeren'!C2","v":7.431676275425577}]
[null,"Lgem=opp/D",null,null,{"$f":"0.25*PI()*'Gegevens invoeren'!C2","v":35.342917352885173}]
[null,"T1",null,{"$f":"'Gegevens invoeren'!C3","v":50},43.568502523932445,40.502060175508575]
[null,"T2",null,{"$f":"D21-D29*'Gegevens invoeren'!C24/Database!I13","v":49.996779666424949},{"$f":"E21-E29*'Gegevens invoeren'!C24/50","v":43.566850192751133}]
[null,"T3",null,{"$f":"D21-D28*D11","v":12.551306994403802},{"$f":"E21-E27*E11","v":11.544927304284386},{"$f":"F21-F27*F11","v":12.125920339196941}]
[null,"T4",null,12.551306994403799,{"$f":"E23-E27*'Gegevens invoeren'!C11/237","v":11.544927304284386}]
[null,"Tf",null,{"$f":"(D24+'Gegevens invoeren'!B30)/2","v":11.672231366054355},{"$f":"(E24+'Gegevens invoeren'!B30)/2","v":11.169041520994647},{"$f":"(F23+'Gegevens invoeren'!B30)/2","v":11.459538038450926}]
[null,"geldig?",null,{"$f":"IF(D17*D6>0.2,1,0)","v":1},{"$f":"IF(E17>500000,IF(E14>320000,1,0),0)","v":1},{"$f":"E26*D26","v":1}]
["W/m2","q in",null,null,{"$f":"E16*('Gegevens invoeren'!C3-E21)","v":8.2616561052141702},{"$f":"F16*('Gegevens invoeren'!C3-F21)","v":12.200690870199164}]
["W/m2","q wand",{"$f":"1/C11*('Gegevens invoeren'!C3-'Gegevens invoeren'!C25)","v":39.735099337748345},{"$f":"1/D11*('Gegevens invoeren'!C3-D24)","v":16.101553258826105},{"$f":"1/E11*(E21-E23)","v":8.2616561052141702},{"$f":"1/F11*(F21-F23)","v":12.200690870199166}]
["W/m2","q uit",null,{"$f":"D19*(D24-'Gegevens invoeren'!B30)+0.0000000567*'Gegevens invoeren'!B33*((273+D24)^4-(273+'Gegevens invoeren'!B30)^4)","v":16.10166787526768},{"$f":"E19*(E23-'Gegevens invoeren'!B30)+0.0000000567*'Gegevens invoeren'!B33*((273+E23)^4-(273+'Gegevens invoeren'!B30)^4)","v":8.2616559065740258},{"$f":"F19*(F23-'Gegevens invoeren'!B30)+0.0000000567*'Gegevens invoeren'!B33*((273+F23)^4-(273+'Gegevens invoeren'!B30)^4)","v":12.200687970483724}]
[null,null,null,{"$f":"D28-D29","v":-1.1461644157506612E-4},{"$f":"E28-E29","v":1.9864014433323973E-7},{"$f":"F28-F29","v":2.8997154419840854E-6}]

{"sheet":"Database","index":2,"n_rows":57,"n_cols":25,"rows_kept":57,"cut":false,"hidden":false,"merged":[]}
["Tankgegevens",null,null,null,null,"Weersstation",null,"thermofysische eigenschappen"]
["isolatie","kleur","dak","factor",null,null,null,null,"k",null,"emissiefactor"]
["steen- of glaswol","wit","dome",1.0720000000000001,null,"De Bilt",null,"steen- of glaswol",{"$f":"0.035","v":3.5000000000000003E-2},null,"witte verf",0.9]
["PIR","aluminium","conisch",1.0349999999999999,null,"De Kooy",null,"PUR",0.03,null,"aluminium verf",0.45]
["PUR","zwart","plat",1,null,"Deelen",null,"PIR",2.3E-2,null,"aluminium",0.33]
["isolerende verf","roestbruin",null,null,null,"Eindhoven",null,"RVS",16,null,"staal verroest",0.81]
[null,null,null,null,null,"Lauwersoog",null,"alu",237,null,"staal",0.32]
[null,null,null,null,null,"Leeuwarden",null,"zand",1,null,"zwarte verf",0.98]
[null,null,null,null,null,"Maastricht",null,"beton",1.9,null,"isolerende verf",0.85]
[null,null,null,null,null,"Rotterdam",null,"zandbitumen",0.6,null,"RVS",0.75]
[null,null,null,null,null,"Twenthe",null,"klei",1.6]
[null,null,null,null,null,"Vlissingen",null,"foamglas",4.4999999999999998E-2]
[null,null,null,null,null,null,null,"staal",50]
[null,null,null,null,null,null,null,"aluminium",237]
["Luchtgegevens",null,null,null,null,null,null,"isolerende verf",0.05]
[]
[null,-10,0,10,20,30,40,50,60,70,80,90,100,110,120,130,140,150,160,170,180,190,200,210,220]
[null,{"$f":"B17+273","v":263},273,283,293,303,313,323,333,343,353,363,373,383,393,403,413,423,433,443,453,463,473,483,493]
["rho",{"$f":" -(1.39-0.995)/100*B18+2.38","v":1.3411500000000003},1.3016500000000002,1.2621500000000003,1.2226500000000002,1.1831500000000004,1.1436500000000003,1.1041500000000004,1.0646500000000003,1.0251500000000004,0.98565000000000036,0.94615000000000049,0.9066500000000004,0.86715000000000031,0.82765000000000044,0.78815000000000035,0.74865000000000048,0.70915000000000039,0.66965000000000052,0.63015000000000043,{"$f":" -(1.39-0.995)/100*U18+2.38","v":0.59065000000000056},{"$f":" -(1.39-0.995)/100*V18+2.38","v":0.55115000000000047},{"$f":" -(1.39-0.995)/100*W18+2.38","v":0.5116500000000006},{"$f":" -(1.39-0.995)/100*X18+2.38","v":0.47215000000000051},{"$f":" -(1.39-0.995)/100*Y18+2.38","v":0.43265000000000065}]
["Pr",{"$f":"B21*B19*B24/B22","v":0.73188753913126048},{"$f":"C21*C19*C24/C22","v":0.7395294733506087},0.74367313104333566,0.74463140408310879,0.74268065400089101,0.73806589197165873,0.7310051016850222,{"$f":"I21*I19*I24/I22","v":0.72169286612082206},{"$f":"J21*J19*J24/J22","v":0.71030342558288928},{"$f":"K21*K19*K24/K22","v":0.69699326839411535},0.68190333550683846,0.66516090452842236,0.64688120626279155,0.62716881704909822,0.60611886235578505,0.5838180608209953,0.5603456328822185,0.53577409405134535,0.51016994956668305,0.48359430443627932,0.45610340065624938,0.42774909154879576,0.39857926164229307,0.36863819925075031]
["vouw",{"$f":" (0.0000209-0.0000114)/100*B18-0.00001235","v":1.2635000000000002E-5},1.3585000000000001E-5,1.4535000000000001E-5,1.5484999999999998E-5,1.6435000000000001E-5,1.7385000000000004E-5,1.8335E-5,1.9285000000000003E-5,2.0234999999999999E-5,2.1185000000000001E-5,2.2134999999999997E-5,2.3085E-5,2.4034999999999996E-5,2.4984999999999999E-5,2.5935000000000002E-5,2.6884999999999998E-5,2.7835E-5,2.8784999999999996E-5,2.9734999999999999E-5,{"$f":" (0.0000209-0.0000114)/100*U18-0.00001235","v":3.0685000000000002E-5},{"$f":" (0.0000209-0.0000114)/100*V18-0.00001235","v":3.1634999999999998E-5},{"$f":" (0.0000209-0.0000114)/100*W18-0.00001235","v":3.2585000000000001E-5},{"$f":" (0.0000209-0.0000114)/100*X18-0.00001235","v":3.3534999999999997E-5},{"$f":" (0.0000209-0.0000114)/100*Y18-0.00001235","v":3.4484999999999999E-5}]
["k",{"$f":" (0.03-0.0223)/100*B18+0.00305","v":2.3300999999999999E-2},2.4070999999999999E-2,2.4840999999999998E-2,2.5610999999999998E-2,2.6380999999999998E-2,2.7150999999999998E-2,2.7920999999999998E-2,2.8690999999999998E-2,2.9460999999999998E-2,3.0230999999999997E-2,3.1000999999999997E-2,3.1770999999999994E-2,3.2540999999999994E-2,3.3310999999999993E-2,3.4080999999999993E-2,3.4850999999999993E-2,3.5620999999999993E-2,3.6390999999999993E-2,3.7160999999999993E-2,{"$f":" (0.03-0.0223)/100*U18+0.00305","v":3.7930999999999993E-2},{"$f":" (0.03-0.0223)/100*V18+0.00305","v":3.8700999999999992E-2},{"$f":" (0.03-0.0223)/100*W18+0.00305","v":3.9470999999999992E-2},{"$f":" (0.03-0.0223)/100*X18+0.00305","v":4.0240999999999992E-2},{"$f":" (0.03-0.0223)/100*Y18+0.00305","v":4.1010999999999992E-2}]
["Cp",{"$f":" (1.009-1.006)/100*B18+0.9985","v":1.0063899999999997},{"$f":" (1.009-1.006)/100*C18+0.9985","v":1.0066899999999999},1.0069899999999998,1.0072899999999998,1.0075899999999998,1.0078899999999997,1.0081899999999997,{"$f":" (1.009-1.006)/100*I18+0.9985","v":1.0084899999999997},{"$f":" (1.009-1.006)/100*J18+0.9985","v":1.0087899999999996},{"$f":" (1.009-1.006)/100*K18+0.9985","v":1.0090899999999996},{"$f":" (1.009-1.006)/100*L18+0.9985","v":1.0093899999999996},{"$f":" (1.009-1.006)/100*M18+0.9985","v":1.0096899999999998},1.0099899999999997,1.0102899999999997,1.0105899999999997,1.0108899999999996,1.0111899999999996,1.0114899999999996,1.0117899999999995,{"$f":" (1.009-1.006)/100*U18+0.9985","v":1.0120899999999995},{"$f":" (1.009-1.006)/100*V18+0.9985","v":1.0123899999999995},{"$f":" (1.009-1.006)/100*W18+0.9985","v":1.0126899999999996},{"$f":" (1.009-1.006)/100*X18+0.9985","v":1.0129899999999996},{"$f":" (1.009-1.006)/100*Y18+0.9985","v":1.0132899999999996}]
["Cp in J/kgK",{"$f":"B23*1000","v":1006.3899999999996},1006.6899999999998,1006.9899999999998,1007.2899999999998,1007.5899999999998,1007.8899999999998,1008.1899999999997,1008.4899999999997,1008.7899999999996,1009.0899999999996,1009.3899999999995,1009.6899999999997,1009.9899999999997,1010.2899999999997,1010.5899999999997,1010.8899999999996,1011.1899999999996,1011.4899999999996,1011.7899999999995,1012.0899999999995,1012.3899999999994,1012.6899999999996,1012.9899999999997,1013.2899999999996]
[]
[]
["Stoomgegevens"]
[null,"Temperatuur"]
["Absolute","verzadigde","Vloeistof","Verdampings","Totale","Soortelijk"]
["druk","stoom","warmte","warmte","warmte","volume"]
["Bar","°C","kJ/kg","kJ/kg","kJ/kg","m3/kg"]
[6.6,162.6,686.78,2072.6999999999998,2759.5,0.28799999999999998]
[6.8,163.79,691.98,2068.8000000000002,"2.760.8",0.28000000000000003]
[7,164.96,697.06,2064.9,2762,0.27300000000000002]
[7.2,166.1,702.03,2061.1,2763.2,0.26600000000000001]
[7.4,167.21,706.9,2057.4,2764.3,0.25900000000000001]
[7.6,168.3,711.68,2053.6999999999998,2765.4,0.252]
[7.8,169.37,716.35,2050.1,2766.4,0.246]
[8,170.41,720.94,2046.5,2767.5,0.24]
[8.1999999999999993,171.44,725.43,2043,2768.5,0.23499999999999999]
[8.4,172.45,729.85,2039.6,2769.4,0.22900000000000001]
[8.6,173.44,734.19,2036.2,2770.4,0.224]
[8.8000000000000007,174.41,738.45,2032.8,2771.3,0.22]
[9,175.36,742.64,2029.5,2772.1,0.215]
[9.1999999999999993,176.29,746.76,2026.2,2773,0.21]
[9.4,177.21,750.82,2023,2773.8,0.20599999999999999]
[9.6,178.12,754.81,2019.8,2774.6,0.20200000000000001]
[9.8000000000000007,179.01,758.74,2016.7,2775.4,0.19800000000000001]
[10,179.88,762.61,2013.6,2776.2,0.19400000000000001]
[10.5,182.02,772.03,2005.9,2778,0.186]
[11,184.07,781.13,1998.5,2779.7,0.17699999999999999]
[11.5,186.05,789.92,1991.3,2781.3,0.17]
[12,187.96,798.43,1984.3,2782.7,0.16300000000000001]
[12.5,189.81,806.69,1977.4,2784.1,0.157]
[13,191.61,814.7,1970.7,2785.4,0.151]
[13.5,193.35,822.49,1964.2,2786.6,0.14599999999999999]
[14,195.04,830.08,1957.7,2787.8,0.14099999999999999]

{"sheet":"Weersgegevens","index":3,"n_rows":3662,"n_cols":7,"rows_kept":3662,"cut":false,"hidden":false,"merged":[]}
["# BRON: KONINKLIJK NEDERLANDS METEOROLOGISCH INSTITUUT (KNMI)",null,null,null,null,null,"Gemiddelde van 2000 t/m 2014. Voor meer weergegevens zie: http://www.knmi.nl/klimatologie/daggegevens/selectie.cgi"]
["key","Station","maand","dag","wind","temperatuur"]
["De Bilt0101","De Bilt","01","01",4.0133333333333336,4.1333333333333337]
["De Bilt0102","De Bilt","01","02",3.746666666666667,3.8333333333333335]
["De Bilt0103","De Bilt","01","03",4.3,3.2333333333333334]
["De Bilt0104","De Bilt","01","04",4.6466666666666656,3.8533333333333331]
["De Bilt0105","De Bilt","01","05",4.2799999999999994,3.58]
["De Bilt0106","De Bilt","01","06",3.7400000000000007,4.246666666666667]
["De Bilt0107","De Bilt","01","07",4.12,4.5199999999999996]
["De Bilt0108","De Bilt","01","08",4.4266666666666667,3.9666666666666668]
["De Bilt0109","De Bilt","01","09",3.9999999999999996,3.1333333333333337]
["De Bilt0110","De Bilt","01","10",3.8133333333333335,3.1533333333333333]
["De Bilt0111","De Bilt","01","11",4.3000000000000007,3.8866666666666663]
["De Bilt0112","De Bilt","01","12",4.1999999999999993,3.5599999999999996]
["De Bilt0113","De Bilt","01","13",4.4066666666666663,4.0733333333333333]
["De Bilt0114","De Bilt","01","14",3.5333333333333332,3.5399999999999996]
["De Bilt0115","De Bilt","01","15",4.0733333333333333,2.9799999999999995]
["De Bilt0116","De Bilt","01","16",3.9133333333333336,3.1133333333333337]
["De Bilt0117","De Bilt","01","17",4.1066666666666665,4.0733333333333341]
["De Bilt0118","De Bilt","01","18",4.3733333333333331,4.3]
["De Bilt0119","De Bilt","01","19",4.22,4.9333333333333336]
["De Bilt0120","De Bilt","01","20",4.84,5.0999999999999996]
["De Bilt0121","De Bilt","01","21",4.1866666666666665,4.6266666666666669]
["De Bilt0122","De Bilt","01","22",3.9866666666666668,3.46]
["De Bilt0123","De Bilt","01","23",3.7266666666666661,2.7266666666666666]
["De Bilt0124","De Bilt","01","24",3.1733333333333333,2.5933333333333333]
["De Bilt0125","De Bilt","01","25",3.6599999999999997,1.9599999999999997]
["De Bilt0126","De Bilt","01","26",4.2466666666666661,2.4666666666666668]
["De Bilt0127","De Bilt","01","27",3.7866666666666666,3.226666666666667]
["De Bilt0128","De Bilt","01","28",4.3933333333333326,3.5200000000000009]
["De Bilt0129","De Bilt","01","29",4.1933333333333334,3.3533333333333326]
["De Bilt0130","De Bilt","01","30",3.6933333333333329,3.5066666666666668]
["De Bilt0131","De Bilt","01","31",4.7666666666666657,3.2800000000000002]
["De Bilt0201","De Bilt","02","01",4.6466666666666674,3.2066666666666666]
["De Bilt0202","De Bilt","02","02",4.4799999999999995,3.8266666666666671]
["De Bilt0203","De Bilt","02","03",3.74,4.04]
["De Bilt0204","De Bilt","02","04",4.3933333333333326,4.7799999999999985]
["De Bilt0205","De Bilt","02","05",4.8666666666666663,5.3533333333333344]
["De Bilt0206","De Bilt","02","06",4.1733333333333338,4.7333333333333325]
["De Bilt0207","De Bilt","02","07",4.24,4.0733333333333341]
["De Bilt0208","De Bilt","02","08",4.3266666666666671,3.8066666666666658]
["De Bilt0209","De Bilt","02","09",4.1466666666666665,3.226666666666667]
["De Bilt0210","De Bilt","02","10",4.12,3.2]
["De Bilt0211","De Bilt","02","11",4.0133333333333328,3.813333333333333]
["De Bilt0212","De Bilt","02","12",4.0733333333333333,3.7533333333333334]
["De Bilt0213","De Bilt","02","13",3.3133333333333335,3.4800000000000009]
["De Bilt0214","De Bilt","02","14",3.4666666666666672,3.08]
["De Bilt0215","De Bilt","02","15",3.8266666666666671,3.9133333333333331]
["De Bilt0216","De Bilt","02","16",3.5133333333333332,3.4133333333333336]
["De Bilt0217","De Bilt","02","17",2.9666666666666672,3.0533333333333332]
["De Bilt0218","De Bilt","02","18",3.0599999999999996,3.2466666666666675]
["De Bilt0219","De Bilt","02","19",3.813333333333333,3.4933333333333327]
["De Bilt0220","De Bilt","02","20",3.8600000000000003,3.2]
["De Bilt0221","De Bilt","02","21",3.9333333333333331,3.2800000000000002]
["De Bilt0222","De Bilt","02","22",4.58,3.9400000000000004]
["De Bilt0223","De Bilt","02","23",3.9533333333333331,3.9533333333333336]
["De Bilt0224","De Bilt","02","24",3.813333333333333,4.58]
["De Bilt0225","De Bilt","02","25",3.7200000000000006,4.5666666666666664]
["De Bilt0226","De Bilt","02","26",4.2666666666666666,5.2333333333333334]
["De Bilt0227","De Bilt","02","27",4.2666666666666666,4.5466666666666669]
["De Bilt0228","De Bilt","02","28",3.6599999999999997,4.9133333333333331]
["De Bilt0229","De Bilt","02","29",4.3249999999999993,5.5500000000000007]
["De Bilt0301","De Bilt","03","01",3.9133333333333336,4.6800000000000015]
["De Bilt0302","De Bilt","03","02",3.5733333333333328,4.18]
["De Bilt0303","De Bilt","03","03",3.4066666666666663,3.5000000000000004]
["De Bilt0304","De Bilt","03","04",3.526666666666666,3.56]
["De Bilt0305","De Bilt","03","05",3.32,4.5466666666666669]
["De Bilt0306","De Bilt","03","06",4.0733333333333333,4.9733333333333327]
["De Bilt0307","De Bilt","03","07",3.8999999999999995,5.62]
["De Bilt0308","De Bilt","03","08",4.1999999999999993,6.54]
["De Bilt0309","De Bilt","03","09",4.4000000000000004,6.8066666666666666]
["De Bilt0310","De Bilt","03","10",4.333333333333333,5.9733333333333327]
["De Bilt0311","De Bilt","03","11",4.4133333333333331,6.206666666666667]
["De Bilt0312","De Bilt","03","12",3.5866666666666673,5.88]
["De Bilt0313","De Bilt","03","13",3.1933333333333334,5.7933333333333339]
["De Bilt0314","De Bilt","03","14",3.4266666666666672,5.793333333333333]
["De Bilt0315","De Bilt","03","15",4.08,6.7266666666666675]
["De Bilt0316","De Bilt","03","16",3.7599999999999993,7.98]
["De Bilt0317","De Bilt","03","17",3.8533333333333339,7.3466666666666667]
["De Bilt0318","De Bilt","03","18",3.7399999999999998,6.6800000000000015]
["De Bilt0319","De Bilt","03","19",3.5799999999999996,6.1466666666666647]
["De Bilt0320","De Bilt","03","20",3.7,6.4866666666666664]
["De Bilt0321","De Bilt","03","21",3.4466666666666668,6.0066666666666659]
["De Bilt0322","De Bilt","03","22",3.6866666666666665,6.2399999999999993]
["De Bilt0323","De Bilt","03","23",3.5266666666666668,6.3666666666666663]
["De Bilt0324","De Bilt","03","24",3.4933333333333341,6.9333333333333336]
["De Bilt0325","De Bilt","03","25",3.6133333333333328,7.0933333333333328]
["De Bilt0326","De Bilt","03","26",3.3133333333333326,6.98]
["De Bilt0327","De Bilt","03","27",3.6533333333333333,7.2666666666666657]
["De Bilt0328","De Bilt","03","28",3.7666666666666666,7.7199999999999989]
["De Bilt0329","De Bilt","03","29",3.0933333333333328,7.8333333333333321]
["De Bilt0330","De Bilt","03","30",3.44,8.5466666666666651]
["De Bilt0331","De Bilt","03","31",3.8266666666666662,8.9199999999999982]
["De Bilt0401","De Bilt","04","01",3.7999999999999989,9.2266666666666648]
["De Bilt0402","De Bilt","04","02",4.04,10.533333333333333]
["De Bilt0403","De Bilt","04","03",3.7933333333333321,10.079999999999997]
["De Bilt0404","De Bilt","04","04",3.8866666666666663,8.7066666666666652]
["De Bilt0405","De Bilt","04","05",4.16,7.6666666666666687]
["De Bilt0406","De Bilt","04","06",3.8133333333333321,8.2799999999999994]
["De Bilt0407","De Bilt","04","07",3.3400000000000007,8.0333333333333332]
["De Bilt0408","De Bilt","04","08",3.373333333333334,7.0933333333333337]
["De Bilt0409","De Bilt","04","09",3.2533333333333334,7.7200000000000006]
["De Bilt0410","De Bilt","04","10",3.2400000000000007,8.5133333333333319]
["De Bilt0411","De Bilt","04","11",3.1066666666666669,8.706666666666667]
["De Bilt0412","De Bilt","04","12",3.46,8.6199999999999992]
["De Bilt0413","De Bilt","04","13",3.4999999999999996,9.1999999999999993]
["De Bilt0414","De Bilt","04","14",3.1799999999999997,9.8333333333333339]
["De Bilt0415","De Bilt","04","15",3.3666666666666671,10.526666666666667]
["De Bilt0416","De Bilt","04","16",3.06,10.146666666666667]
["De Bilt0417","De Bilt","04","17",3.4133333333333331,10.533333333333331]
["De Bilt0418","De Bilt","04","18",4.3266666666666671,9.84]
["De Bilt0419","De Bilt","04","19",3.5666666666666669,9.3733333333333331]
["De Bilt0420","De Bilt","04","20",3.2066666666666661,10.113333333333333]
["De Bilt0421","De Bilt","04","21",2.9066666666666667,10.793333333333335]
["De Bilt0422","De Bilt","04","22",2.686666666666667,10.946666666666667]
["De Bilt0423","De Bilt","04","23",2.56,11.513333333333334]
["De Bilt0424","De Bilt","04","24",2.5933333333333328,12.919999999999998]
["De Bilt0425","De Bilt","04","25",3.1199999999999997,13.853333333333333]
["De Bilt0426","De Bilt","04","26",3.2733333333333325,12.566666666666665]
["De Bilt0427","De Bilt","04","27",3.6133333333333328,12.613333333333335]
["De Bilt0428","De Bilt","04","28",3.4066666666666663,12.526666666666666]
["De Bilt0429","De Bilt","04","29",3.5599999999999996,12.580000000000002]
["De Bilt0430","De Bilt","04","30",3.5933333333333333,12.693333333333333]
["De Bilt0501","De Bilt","05","01",3.8933333333333326,12.640000000000004]
["De Bilt0502","De Bilt","05","02",3.5066666666666668,11.813333333333336]
["De Bilt0503","De Bilt","05","03",3.2599999999999989,11.746666666666666]
["De Bilt0504","De Bilt","05","04",3.56,11.6]
["De Bilt0505","De Bilt","05","05",3.4333333333333331,12.079999999999997]
["De Bilt0506","De Bilt","05","06",3.4799999999999991,13.18]
["De Bilt0507","De Bilt","05","07",3.4799999999999995,13.486666666666668]
["De Bilt0508","De Bilt","05","08",3.5799999999999996,13.846666666666668]
["De Bilt0509","De Bilt","05","09",3.0533333333333332,14.38]
["De Bilt0510","De Bilt","05","10",3.4,14.48]
["De Bilt0511","De Bilt","05","11",3.8266666666666667,13.426666666666668]
["De Bilt0512","De Bilt","05","12",3.5599999999999996,12.8]
["De Bilt0513","De Bilt","05","13",3.373333333333334,13.52]
["De Bilt0514","De Bilt","05","14",3.3266666666666667,12.76]
["De Bilt0515","De Bilt","05","15",2.9133333333333336,12.939999999999998]
["De Bilt0516","De Bilt","05","16",3,12.826666666666663]
["De Bilt0517","De Bilt","05","17",3.0933333333333337,12.506666666666664]
["De Bilt0518","De Bilt","05","18",3.3066666666666662,12.926666666666668]
["De Bilt0519","De Bilt","05","19",3.3533333333333331,13.086666666666668]
["De Bilt0520","De Bilt","05","20",2.9666666666666672,13.780000000000003]
["De Bilt0521","De Bilt","05","21",3.1266666666666665,14.353333333333333]
["De Bilt0522","De Bilt","05","22",3.4533333333333336,14.273333333333333]
["De Bilt0523","De Bilt","05","23",3.0733333333333333,14.4]
["De Bilt0524","De Bilt","05","24",3.4533333333333331,14.566666666666666]
["De Bilt0525","De Bilt","05","25",3.413333333333334,14.580000000000002]
["De Bilt0526","De Bilt","05","26",3.6733333333333333,14.12]
["De Bilt0527","De Bilt","05","27",3.2399999999999998,14.58]
["De Bilt0528","De Bilt","05","28",3.5666666666666673,14.8]
["De Bilt0529","De Bilt","05","29",3.36,13.833333333333334]
["De Bilt0530","De Bilt","05","30",2.7000000000000006,14.246666666666666]
["De Bilt0531","De Bilt","05","31",3.0000000000000004,14.080000000000002]
["De Bilt0601","De Bilt","06","01",2.6399999999999997,14.546666666666663]
["De Bilt0602","De Bilt","06","02",3.1333333333333333,15.479999999999999]
["De Bilt0603","De Bilt","06","03",3.0933333333333337,15.326666666666664]
["De Bilt0604","De Bilt","06","04",3.2533333333333334,15.406666666666666]
["De Bilt0605","De Bilt","06","05",2.8600000000000003,14.846666666666664]
["De Bilt0606","De Bilt","06","06",2.78,15.513333333333334]
["De Bilt0607","De Bilt","06","07",2.9799999999999995,15.913333333333332]
["De Bilt0608","De Bilt","06","08",3.0066666666666664,16.59333333333333]
["De Bilt0609","De Bilt","06","09",2.9533333333333331,16.580000000000002]
["De Bilt0610","De Bilt","06","10",2.54,16.099999999999998]
["De Bilt0611","De Bilt","06","11",3.0733333333333328,15.546666666666665]
["De Bilt0612","De Bilt","06","12",2.9,15.233333333333333]
["De Bilt0613","De Bilt","06","13",2.88,15.493333333333336]
["De Bilt0614","De Bilt","06","14",2.8599999999999994,15.98]
["De Bilt0615","De Bilt","06","15",3.2,15.706666666666669]
["De Bilt0616","De Bilt","06","16",3.1,15.320000000000002]
["De Bilt0617","De Bilt","06","17",3.0799999999999996,16.833333333333336]
["De Bilt0618","De Bilt","06","18",3.1066666666666665,17.359999999999996]
["De Bilt0619","De Bilt","06","19",3.273333333333333,17.180000000000003]
["De Bilt0620","De Bilt","06","20",3.1333333333333329,17.133333333333333]
["De Bilt0621","De Bilt","06","21",3.2266666666666666,16.213333333333335]
["De Bilt0622","De Bilt","06","22",3.6333333333333329,16.240000000000002]
["De Bilt0623","De Bilt","06","23",3.6600000000000006,16.486666666666668]
["De Bilt0624","De Bilt","06","24",3.1599999999999993,16.52]
["De Bilt0625","De Bilt","06","25",3.14,16.080000000000002]
["De Bilt0626","De Bilt","06","26",2.8933333333333326,16.746666666666663]
["De Bilt0627","De Bilt","06","27",3.1333333333333337,17.426666666666666]
["De Bilt0628","De Bilt","06","28",3.1066666666666669,17.613333333333337]
["De Bilt0629","De Bilt","06","29",3.0066666666666673,17.033333333333335]
["De Bilt0630","De Bilt","06","30",2.8466666666666667,17.406666666666663]
["De Bilt0701","De Bilt","07","01",3.1600000000000006,17.32]
["De Bilt0702","De Bilt","07","02",2.9666666666666663,18.293333333333337]
["De Bilt0703","De Bilt","07","03",3.253333333333333,18.319999999999997]
["De Bilt0704","De Bilt","07","04",3.1133333333333337,18.38]
["De Bilt0705","De Bilt","07","05",2.8266666666666667,18.48]
["De Bilt0706","De Bilt","07","06",2.973333333333334,17.893333333333331]
["De Bilt0707","De Bilt","07","07",3.273333333333333,17.326666666666668]
["De Bilt0708","De Bilt","07","08",3,17.02]
["De Bilt0709","De Bilt","07","09",3.3,17.22666666666667]
["De Bilt0710","De Bilt","07","10",3.1733333333333333,17.720000000000002]
["De Bilt0711","De Bilt","07","11",3.42,17.133333333333333]
["De Bilt0712","De Bilt","07","12",3.1333333333333329,16.66]
["De Bilt0713","De Bilt","07","13",2.9066666666666672,17.16]
["De Bilt0714","De Bilt","07","14",3.2666666666666666,17.606666666666669]
["De Bilt0715","De Bilt","07","15",3.22,18.399999999999999]
["De Bilt0716","De Bilt","07","16",3,18.706666666666667]
["De Bilt0717","De Bilt","07","17",3.1933333333333338,18.306666666666668]
["De Bilt0718","De Bilt","07","18",3.5066666666666664,18.326666666666668]
["De Bilt0719","De Bilt","07","19",3.0133333333333332,18.886666666666663]
["De Bilt0720","De Bilt","07","20",2.7800000000000002,18.046666666666667]
["De Bilt0721","De Bilt","07","21",2.8866666666666663,17.913333333333334]
["De Bilt0722","De Bilt","07","22",2.5733333333333333,18.326666666666664]
["De Bilt0723","De Bilt","07","23",2.7133333333333329,18.393333333333334]
["De Bilt0724","De Bilt","07","24",3.0333333333333337,18.280000000000005]
["De Bilt0725","De Bilt","07","25",2.74,18.59333333333333]
["De Bilt0726","De Bilt","07","26",2.4399999999999995,19.133333333333329]
["De Bilt0727","De Bilt","07","27",2.2999999999999998,19.473333333333333]
["De Bilt0728","De Bilt","07","28",2.46,19.486666666666665]
["De Bilt0729","De Bilt","07","29",2.6133333333333337,19.246666666666666]
["De Bilt0730","De Bilt","07","30",2.9066666666666663,18.406666666666663]
["De Bilt0731","De Bilt","07","31",2.4,18.100000000000001]
["De Bilt0801","De Bilt","08","01",2.5066666666666664,18.773333333333333]
["De Bilt0802","De Bilt","08","02",2.58,18.779999999999998]
["De Bilt0803","De Bilt","08","03",2.5066666666666664,18.093333333333337]
["De Bilt0804","De Bilt","08","04",2.8,18.59333333333333]
["De Bilt0805","De Bilt","08","05",2.6333333333333333,18.966666666666665]
["De Bilt0806","De Bilt","08","06",2.7733333333333334,19.206666666666667]
["De Bilt0807","De Bilt","08","07",2.7133333333333329,18.426666666666666]
["De Bilt0808","De Bilt","08","08",2.9399999999999995,17.866666666666667]
["De Bilt0809","De Bilt","08","09",2.9533333333333331,17.686666666666667]
["De Bilt0810","De Bilt","08","10",3.0933333333333337,17.486666666666668]
["De Bilt0811","De Bilt","08","11",2.9199999999999995,17.586666666666666]
["De Bilt0812","De Bilt","08","12",2.973333333333334,17.313333333333333]
["De Bilt0813","De Bilt","08","13",3.186666666666667,17.446666666666665]
["De Bilt0814","De Bilt","08","14",2.6399999999999997,17.98]
["De Bilt0815","De Bilt","08","15",2.9933333333333332,18.25333333333333]
["De Bilt0816","De Bilt","08","16",2.5533333333333332,18.013333333333328]
["De Bilt0817","De Bilt","08","17",2.9799999999999995,17.993333333333332]
["De Bilt0818","De Bilt","08","18",3.0466666666666664,18.746666666666666]
["De Bilt0819","De Bilt","08","19",3.1533333333333333,18.526666666666664]
["De Bilt0820","De Bilt","08","20",2.6199999999999997,17.68]
["De Bilt0821","De Bilt","08","21",2.7266666666666666,17.419999999999998]
["De Bilt0822","De Bilt","08","22",2.5533333333333332,16.946666666666665]
["De Bilt0823","De Bilt","08","23",2.6999999999999997,17.453333333333333]
["De Bilt0824","De Bilt","08","24",2.68,17.426666666666669]
["De Bilt0825","De Bilt","08","25",2.7666666666666666,17.266666666666666]
["De Bilt0826","De Bilt","08","26",3.1933333333333334,17.180000000000003]
["De Bilt0827","De Bilt","08","27",2.7866666666666662,16.366666666666667]
["De Bilt0828","De Bilt","08","28",2.746666666666667,15.839999999999998]
["De Bilt0829","De Bilt","08","29",2.7466666666666666,15.466666666666667]
["De Bilt0830","De Bilt","08","30",2.8400000000000003,15.620000000000001]
["De Bilt0831","De Bilt","08","31",2.7866666666666671,16.006666666666668]
["De Bilt0901","De Bilt","09","01",2.5866666666666664,15.300000000000002]
["De Bilt0902","De Bilt","09","02",2.82,15.98]
["De Bilt0903","De Bilt","09","03",3.046666666666666,16.346666666666671]
["De Bilt0904","De Bilt","09","04",2.8066666666666666,16.059999999999999]
["De Bilt0905","De Bilt","09","05",2.7733333333333334,16.553333333333335]
["De Bilt0906","De Bilt","09","06",3.2133333333333329,16.959999999999997]
["De Bilt0907","De Bilt","09","07",3.253333333333333,16.153333333333329]
["De Bilt0908","De Bilt","09","08",2.72,15.900000000000002]
["De Bilt0909","De Bilt","09","09",2.6266666666666669,16.046666666666667]
["De Bilt0910","De Bilt","09","10",2.8466666666666662,16.12]
["De Bilt0911","De Bilt","09","11",2.9533333333333336,16.566666666666666]
["De Bilt0912","De Bilt","09","12",3.066666666666666,15.74666666666667]
["De Bilt0913","De Bilt","09","13",2.8533333333333335,14.979999999999999]
["De Bilt0914","De Bilt","09","14",3.3399999999999994,14.933333333333332]
["De Bilt0915","De Bilt","09","15",2.8733333333333331,14.480000000000002]
["De Bilt0916","De Bilt","09","16",2.686666666666667,14.106666666666666]
["De Bilt0917","De Bilt","09","17",2.546666666666666,13.74]
["De Bilt0918","De Bilt","09","18",2.5133333333333336,13.806666666666668]
["De Bilt0919","De Bilt","09","19",2.9066666666666667,13.706666666666669]
["De Bilt0920","De Bilt","09","20",2.8466666666666667,14.3]
["De Bilt0921","De Bilt","09","21",2.6599999999999997,14.58]
["De Bilt0922","De Bilt","09","22",2.96,14.613333333333333]
["De Bilt0923","De Bilt","09","23",2.7199999999999998,13.926666666666668]
["De Bilt0924","De Bilt","09","24",2.8133333333333339,13.573333333333332]
["De Bilt0925","De Bilt","09","25",2.64,13.233333333333336]
["De Bilt0926","De Bilt","09","26",2.4733333333333332,13.273333333333333]
["De Bilt0927","De Bilt","09","27",2.3466666666666667,13.153333333333334]
["De Bilt0928","De Bilt","09","28",2.7933333333333339,13.873333333333331]
["De Bilt0929","De Bilt","09","29",2.8466666666666667,13.686666666666667]
["De Bilt0930","De Bilt","09","30",2.9,13.38]
["De Bilt1001","De Bilt","10","01",3.0533333333333337,13.54]
["De Bilt1002","De Bilt","10","02",3.1533333333333338,13.346666666666668]
["De Bilt1003","De Bilt","10","03",3.3666666666666667,13.919999999999998]
["De Bilt1004","De Bilt","10","04",3.32,13.213333333333333]
["De Bilt1005","De Bilt","10","05",3.2,13.086666666666666]
["De Bilt1006","De Bilt","10","06",3.2999999999999994,12.473333333333334]
["De Bilt1007","De Bilt","10","07",3.0733333333333328,11.653333333333332]
["De Bilt1008","De Bilt","10","08",2.8933333333333331,11.366666666666667]
["De Bilt1009","De Bilt","10","09",3.1933333333333342,11.513333333333332]
["De Bilt1010","De Bilt","10","10",3.7999999999999994,12.000000000000002]
["De Bilt1011","De Bilt","10","11",3.5866666666666669,11.326666666666666]
["De Bilt1012","De Bilt","10","12",3.0333333333333328,11.22]
["De Bilt1013","De Bilt","10","13",2.9133333333333336,11.280000000000001]
["De Bilt1014","De Bilt","10","14",2.96,10.813333333333334]
["De Bilt1015","De Bilt","10","15",3.04,10.526666666666666]
["De Bilt1016","De Bilt","10","16",3.7266666666666666,10.633333333333333]
["De Bilt1017","De Bilt","10","17",3.2866666666666675,10.119999999999999]
["De Bilt1018","De Bilt","10","18",3.1866666666666661,10.486666666666668]
["De Bilt1019","De Bilt","10","19",3.0733333333333337,10.926666666666668]
["De Bilt1020","De Bilt","10","20",3.4333333333333331,10.986666666666668]
["De Bilt1021","De Bilt","10","21",3.8133333333333335,11.213333333333333]
["De Bilt1022","De Bilt","10","22",3.4933333333333332,11.073333333333332]
["De Bilt1023","De Bilt","10","23",3.9133333333333331,10.733333333333333]
["De Bilt1024","De Bilt","10","24",3.7600000000000002,10.253333333333332]
["De Bilt1025","De Bilt","10","25",4.1133333333333333,10.939999999999998]
["De Bilt1026","De Bilt","10","26",3.8266666666666662,10.833333333333334]
["De Bilt1027","De Bilt","10","27",3.9866666666666664,10.126666666666667]
["De Bilt1028","De Bilt","10","28",3.6466666666666669,10.206666666666669]
["De Bilt1029","De Bilt","10","29",3.3933333333333326,10.020000000000001]
["De Bilt1030","De Bilt","10","30",3.4333333333333331,10.219999999999999]
["De Bilt1031","De Bilt","10","31",3.58,10.16]
["De Bilt1101","De Bilt","11","01",3.5733333333333328,9.84]
["De Bilt1102","De Bilt","11","02",3.7533333333333325,10.126666666666667]
["De Bilt1103","De Bilt","11","03",3.9666666666666668,10.373333333333333]
["De Bilt1104","De Bilt","11","04",3.3666666666666667,9.6266666666666669]
["De Bilt1105","De Bilt","11","05",3.2066666666666666,8.9466666666666672]
["De Bilt1106","De Bilt","11","06",3.5400000000000009,9.2133333333333329]
["De Bilt1107","De Bilt","11","07",3.5466666666666664,8.58]
["De Bilt1108","De Bilt","11","08",4.0733333333333333,8.0533333333333328]
["De Bilt1109","De Bilt","11","09",3.4466666666666663,7.1266666666666669]
["De Bilt1110","De Bilt","11","10",3.3933333333333335,7.333333333333333]
["De Bilt1111","De Bilt","11","11",4.2866666666666662,7.7266666666666683]
["De Bilt1112","De Bilt","11","12",3.74,7.8199999999999985]
["De Bilt1113","De Bilt","11","13",3.1199999999999997,7.8666666666666689]
["De Bilt1114","De Bilt","11","14",3.4866666666666664,7.5400000000000009]
["De Bilt1115","De Bilt","11","15",2.82,6.5133333333333336]
["De Bilt1116","De Bilt","11","16",2.7199999999999998,6.7266666666666675]
["De Bilt1117","De Bilt","11","17",3.02,6.96]
["De Bilt1118","De Bilt","11","18",3.2733333333333334,6.94]
["De Bilt1119","De Bilt","11","19",3.0066666666666668,6.64]
["De Bilt1120","De Bilt","11","20",3.4866666666666668,6.76]
["De Bilt1121","De Bilt","11","21",3.933333333333334,6.44]
["De Bilt1122","De Bilt","11","22",3.9399999999999995,6.96]
["De Bilt1123","De Bilt","11","23",3.273333333333333,6.9]
["De Bilt1124","De Bilt","11","24",3.14,6.1800000000000006]
["De Bilt1125","De Bilt","11","25",4.2,6.293333333333333]
["De Bilt1126","De Bilt","11","26",3.6200000000000006,5.8733333333333348]
["De Bilt1127","De Bilt","11","27",3.3466666666666667,5.9]
["De Bilt1128","De Bilt","11","28",3.3400000000000007,5.9333333333333336]
["De Bilt1129","De Bilt","11","29",3.5133333333333336,5.7866666666666662]
["De Bilt1130","De Bilt","11","30",3.1333333333333333,5.1133333333333324]
["De Bilt1201","De Bilt","12","01",4.046666666666666,5.6866666666666656]
["De Bilt1202","De Bilt","12","02",3.3133333333333335,4.5266666666666664]
["De Bilt1203","De Bilt","12","03",3.4133333333333336,4.4533333333333331]
["De Bilt1204","De Bilt","12","04",4.0999999999999996,5.1400000000000006]
["De Bilt1205","De Bilt","12","05",4.1399999999999988,6.28]
["De Bilt1206","De Bilt","12","06",3.8266666666666671,5.5866666666666669]
["De Bilt1207","De Bilt","12","07",4.1666666666666661,4.4666666666666668]
["De Bilt1208","De Bilt","12","08",3.8933333333333331,3.8200000000000003]
["De Bilt1209","De Bilt","12","09",3.6466666666666674,3.3733333333333335]
["De Bilt1210","De Bilt","12","10",3.3733333333333335,2.92]
["De Bilt1211","De Bilt","12","11",3.933333333333334,4.1133333333333333]
["De Bilt1212","De Bilt","12","12",3.8533333333333331,4.1933333333333334]
["De Bilt1213","De Bilt","12","13",4.3,3.4866666666666664]
["De Bilt1214","De Bilt","12","14",3.9,2.9533333333333336]
["De Bilt1215","De Bilt","12","15",4.1266666666666678,3.813333333333333]
["De Bilt1216","De Bilt","12","16",3.6599999999999997,3.5533333333333332]
["De Bilt1217","De Bilt","12","17",3.086666666666666,2.8266666666666671]
["De Bilt1218","De Bilt","12","18",2.8666666666666667,2.3733333333333331]
["De Bilt1219","De Bilt","12","19",3.1799999999999997,2.1800000000000002]
["De Bilt1220","De Bilt","12","20",3.7466666666666666,2.1333333333333337]
["De Bilt1221","De Bilt","12","21",3.62,3.0066666666666664]
["De Bilt1222","De Bilt","12","22",3.7866666666666671,4.0733333333333333]
["De Bilt1223","De Bilt","12","23",4.046666666666666,4.4666666666666668]
["De Bilt1224","De Bilt","12","24",4.4666666666666668,5.22]
["De Bilt1225","De Bilt","12","25",4.0133333333333328,4.8933333333333335]
["De Bilt1226","De Bilt","12","26",3.5466666666666664,3.48]
["De Bilt1227","De Bilt","12","27",4.4599999999999991,3.226666666666667]
["De Bilt1228","De Bilt","12","28",4.22,3.5066666666666664]
["De Bilt1229","De Bilt","12","29",3.899999999999999,3.4399999999999995]
["De Bilt1230","De Bilt","12","30",4.0600000000000005,3.3333333333333335]
["De Bilt1231","De Bilt","12","31",3.8733333333333326,3.6200000000000006]
["De Kooy0101","De Kooy","01","01",6.2866666666666662,4.5266666666666673]
["De Kooy0102","De Kooy","01","02",5.9599999999999991,4.3066666666666666]
["De Kooy0103","De Kooy","01","03",6.8266666666666671,3.7800000000000002]
["De Kooy0104","De Kooy","01","04",7.0199999999999987,4.3133333333333344]
["De Kooy0105","De Kooy","01","05",6.5933333333333328,4.3600000000000003]
["De Kooy0106","De Kooy","01","06",6.0733333333333341,4.7666666666666666]
["De Kooy0107","De Kooy","01","07",6.7600000000000007,4.72]
["De Kooy0108","De Kooy","01","08",7.0600000000000005,4.5866666666666669]
["De Kooy0109","De Kooy","01","09",6.5733333333333333,4.1733333333333329]
["De Kooy0110","De Kooy","01","10",6.993333333333335,3.7933333333333334]
["De Kooy0111","De Kooy","01","11",7.4933333333333314,4.753333333333333]
["De Kooy0112","De Kooy","01","12",7.0066666666666668,4.3866666666666667]
["De Kooy0113","De Kooy","01","13",6.9866666666666664,4.166666666666667]
["De Kooy0114","De Kooy","01","14",5.54,4.0266666666666664]
["De Kooy0115","De Kooy","01","15",6.1799999999999988,3.58]
["De Kooy0116","De Kooy","01","16",6.4266666666666667,3.8466666666666667]
["De Kooy0117","De Kooy","01","17",7.0133333333333319,4.3599999999999994]
["De Kooy0118","De Kooy","01","18",6.4933333333333332,4.666666666666667]
["De Kooy0119","De Kooy","01","19",6.7600000000000007,4.7733333333333325]
["De Kooy0120","De Kooy","01","20",7.6399999999999988,4.88]
["De Kooy0121","De Kooy","01","21",6.7733333333333325,4.3533333333333335]
["De Kooy0122","De Kooy","01","22",6.3133333333333326,3.3866666666666663]
["De Kooy0123","De Kooy","01","23",5.8666666666666663,3.3266666666666662]
["De Kooy0124","De Kooy","01","24",5.166666666666667,3.02]
["De Kooy0125","De Kooy","01","25",5.8733333333333331,2.96]
["De Kooy0126","De Kooy","01","26",6.48,3.3533333333333331]
["De Kooy0127","De Kooy","01","27",6.0466666666666651,3.6999999999999997]
["De Kooy0128","De Kooy","01","28",6.96,3.9866666666666664]
["De Kooy0129","De Kooy","01","29",6.4599999999999991,3.6266666666666665]
["De Kooy0130","De Kooy","01","30",6.0266666666666673,3.6066666666666674]
["De Kooy0131","De Kooy","01","31",7.660000000000001,3.4266666666666667]
["De Kooy0201","De Kooy","02","01",7.5066666666666659,3.5466666666666669]
["De Kooy0202","De Kooy","02","02",7.4266666666666667,4.379999999999999]
["De Kooy0203","De Kooy","02","03",6.3666666666666663,4.0866666666666669]
["De Kooy0204","De Kooy","02","04",6.9066666666666672,3.9733333333333336]
["De Kooy0205","De Kooy","02","05",7.3533333333333308,4.7399999999999993]
["De Kooy0206","De Kooy","02","06",6.54,4.58]
["De Kooy0207","De Kooy","02","07",7.12,4.3]
["De Kooy0208","De Kooy","02","08",7.0866666666666669,3.62]
["De Kooy0209","De Kooy","02","09",6.3,3.3933333333333335]
["De Kooy0210","De Kooy","02","10",6.58,3.2333333333333334]
["De Kooy0211","De Kooy","02","11",5.8066666666666666,3.6066666666666665]
["De Kooy0212","De Kooy","02","12",6.4133333333333331,3.9399999999999995]
["De Kooy0213","De Kooy","02","13",5.0999999999999988,3.7866666666666666]
["De Kooy0214","De Kooy","02","14",5.0666666666666664,3.3533333333333335]
["De Kooy0215","De Kooy","02","15",5.746666666666667,3.9466666666666659]
["De Kooy0216","De Kooy","02","16",5.08,3.6333333333333337]
["De Kooy0217","De Kooy","02","17",4.3266666666666662,3.1866666666666665]
["De Kooy0218","De Kooy","02","18",4.8533333333333335,3.54]
["De Kooy0219","De Kooy","02","19",5.9399999999999995,3.52]
["De Kooy0220","De Kooy","02","20",6.0733333333333333,3.3266666666666671]
["De Kooy0221","De Kooy","02","21",6.333333333333333,3.3800000000000003]
["De Kooy0222","De Kooy","02","22",7.2333333333333334,3.9266666666666654]
["De Kooy0223","De Kooy","02","23",6.5533333333333337,3.7666666666666662]
["De Kooy0224","De Kooy","02","24",5.8266666666666671,4.5200000000000005]
["De Kooy0225","De Kooy","02","25",5.9,4.5466666666666669]
["De Kooy0226","De Kooy","02","26",6.7400000000000011,4.92]
["De Kooy0227","De Kooy","02","27",6.7733333333333343,4.3599999999999994]
["De Kooy0228","De Kooy","02","28",5.6,4.5066666666666668]
["De Kooy0229","De Kooy","02","29",6.7000000000000011,5.2750000000000004]
["De Kooy0301","De Kooy","03","01",5.9333333333333336,4.5200000000000005]
["De Kooy0302","De Kooy","03","02",6.08,3.9733333333333323]
["De Kooy0303","De Kooy","03","03",5.5333333333333332,3.7933333333333339]
["De Kooy0304","De Kooy","03","04",5.24,3.7666666666666666]
["De Kooy0305","De Kooy","03","05",5.1333333333333346,4.84]
["De Kooy0306","De Kooy","03","06",6.2866666666666653,5.166666666666667]
["De Kooy0307","De Kooy","03","07",5.9,5.3933333333333326]
["De Kooy0308","De Kooy","03","08",6.4866666666666664,5.8466666666666676]
["De Kooy0309","De Kooy","03","09",7.3200000000000021,5.8733333333333322]
["De Kooy0310","De Kooy","03","10",7.3200000000000012,5.5600000000000005]
["De Kooy0311","De Kooy","03","11",7.4866666666666672,5.7066666666666679]
["De Kooy0312","De Kooy","03","12",5.6533333333333333,5.5733333333333341]
["De Kooy0313","De Kooy","03","13",4.8933333333333326,5.4866666666666672]
["De Kooy0314","De Kooy","03","14",5.64,5.4866666666666672]
["De Kooy0315","De Kooy","03","15",6.4466666666666663,5.9333333333333336]
["De Kooy0316","De Kooy","03","16",6.453333333333334,6.6066666666666665]
["De Kooy0317","De Kooy","03","17",6.0933333333333337,6.38]
["De Kooy0318","De Kooy","03","18",5.9599999999999991,6.1133333333333333]
["De Kooy0319","De Kooy","03","19",5.56,5.46]
["De Kooy0320","De Kooy","03","20",5.6933333333333334,5.86]
["De Kooy0321","De Kooy","03","21",5.3933333333333335,5.4533333333333323]
["De Kooy0322","De Kooy","03","22",5.3133333333333326,5.7333333333333343]
["De Kooy0323","De Kooy","03","23",5.3266666666666671,5.793333333333333]
["De Kooy0324","De Kooy","03","24",4.9866666666666672,6.3599999999999994]
["De Kooy0325","De Kooy","03","25",5.2333333333333334,6.2200000000000006]
["De Kooy0326","De Kooy","03","26",4.9333333333333327,6.2133333333333338]
["De Kooy0327","De Kooy","03","27",5.74,6.6399999999999988]
["De Kooy0328","De Kooy","03","28",5.7266666666666657,6.8333333333333321]
["De Kooy0329","De Kooy","03","29",4.6800000000000015,7.2600000000000007]
["De Kooy0330","De Kooy","03","30",5.3599999999999994,7.6933333333333325]
["De Kooy0331","De Kooy","03","31",5.6933333333333325,7.78]
["De Kooy0401","De Kooy","04","01",6.1066666666666665,8.2200000000000006]
["De Kooy0402","De Kooy","04","02",5.5466666666666669,9.3000000000000007]
["De Kooy0403","De Kooy","04","03",5.3933333333333326,8.7866666666666671]
["De Kooy0404","De Kooy","04","04",6.2733333333333325,7.6400000000000006]
["De Kooy0405","De Kooy","04","05",6.5733333333333324,7.0933333333333337]
["De Kooy0406","De Kooy","04","06",6.126666666666666,7.5133333333333328]
["De Kooy0407","De Kooy","04","07",4.92,6.9933333333333341]
["De Kooy0408","De Kooy","04","08",5.4533333333333331,6.5200000000000014]
["De Kooy0409","De Kooy","04","09",5.126666666666666,7.2666666666666675]
["De Kooy0410","De Kooy","04","10",4.7,7.86]
["De Kooy0411","De Kooy","04","11",4.5133333333333328,7.9199999999999982]
["De Kooy0412","De Kooy","04","12",5.0733333333333333,8.0599999999999987]
["De Kooy0413","De Kooy","04","13",4.7266666666666657,8.3000000000000025]
["De Kooy0414","De Kooy","04","14",4.7533333333333339,9.1733333333333338]
["De Kooy0415","De Kooy","04","15",4.7066666666666661,9.7666666666666693]
["De Kooy0416","De Kooy","04","16",4.3,9.1333333333333329]
["De Kooy0417","De Kooy","04","17",5.5866666666666651,9.0933333333333337]
["De Kooy0418","De Kooy","04","18",6.2600000000000007,8.9333333333333353]
["De Kooy0419","De Kooy","04","19",5.66,8.9]
["De Kooy0420","De Kooy","04","20",4.7733333333333343,9.68]
["De Kooy0421","De Kooy","04","21",4.3133333333333335,10.053333333333333]
["De Kooy0422","De Kooy","04","22",4.3533333333333335,10.033333333333335]
["De Kooy0423","De Kooy","04","23",3.8000000000000003,10.353333333333333]
["De Kooy0424","De Kooy","04","24",3.9733333333333336,11.833333333333334]
["De Kooy0425","De Kooy","04","25",4.4866666666666664,12.653333333333334]
["De Kooy0426","De Kooy","04","26",5.0866666666666669,11.24]
["De Kooy0427","De Kooy","04","27",5.1866666666666665,11.033333333333331]
["De Kooy0428","De Kooy","04","28",5.62,11.140000000000002]
["De Kooy0429","De Kooy","04","29",5.58,11.033333333333333]
["De Kooy0430","De Kooy","04","30",5.4533333333333331,11.546666666666669]
["De Kooy0501","De Kooy","05","01",5.7666666666666666,11.26]
["De Kooy0502","De Kooy","05","02",5.3866666666666676,10.54]
["De Kooy0503","De Kooy","05","03",4.9399999999999986,10.453333333333331]
["De Kooy0504","De Kooy","05","04",5.2866666666666662,10.740000000000002]
["De Kooy0505","De Kooy","05","05",5.1933333333333334,11.333333333333334]
["De Kooy0506","De Kooy","05","06",5.3466666666666658,12.286666666666667]
["De Kooy0507","De Kooy","05","07",5.42,12.666666666666666]
["De Kooy0508","De Kooy","05","08",5.6933333333333334,12.866666666666669]
["De Kooy0509","De Kooy","05","09",4.78,12.806666666666667]
["De Kooy0510","De Kooy","05","10",5.6199999999999992,13.153333333333332]
["De Kooy0511","De Kooy","05","11",5.9000000000000012,12.173333333333336]
["De Kooy0512","De Kooy","05","12",5.8266666666666662,12.126666666666665]
["De Kooy0513","De Kooy","05","13",5.2666666666666666,12.446666666666665]
["De Kooy0514","De Kooy","05","14",5.7,11.740000000000002]
["De Kooy0515","De Kooy","05","15",4.8,11.906666666666665]
["De Kooy0516","De Kooy","05","16",4.8466666666666667,11.966666666666665]
["De Kooy0517","De Kooy","05","17",5.0333333333333323,11.673333333333334]
["De Kooy0518","De Kooy","05","18",6.0133333333333345,12.139999999999999]
["De Kooy0519","De Kooy","05","19",5.2999999999999989,12.373333333333333]
["De Kooy0520","De Kooy","05","20",4.7133333333333329,12.913333333333334]
["De Kooy0521","De Kooy","05","21",4.7933333333333339,13.06]
["De Kooy0522","De Kooy","05","22",5.4866666666666664,13.359999999999998]
["De Kooy0523","De Kooy","05","23",5.6533333333333333,13.386666666666667]
["De Kooy0524","De Kooy","05","24",5.5533333333333319,13.359999999999998]
["De Kooy0525","De Kooy","05","25",5.253333333333333,13.326666666666664]
["De Kooy0526","De Kooy","05","26",5.92,13.373333333333331]
["De Kooy0527","De Kooy","05","27",5.6533333333333333,13.633333333333333]
["De Kooy0528","De Kooy","05","28",5.8000000000000007,13.593333333333334]
["De Kooy0529","De Kooy","05","29",5.4000000000000012,13.30666666666667]
["De Kooy0530","De Kooy","05","30",4.3133333333333326,13.613333333333335]
["De Kooy0531","De Kooy","05","31",4.5599999999999996,13.000000000000004]
["De Kooy0601","De Kooy","06","01",4.1400000000000006,13.699999999999998]
["De Kooy0602","De Kooy","06","02",4.54,14.393333333333334]
["De Kooy0603","De Kooy","06","03",4.6733333333333329,14.266666666666667]
["De Kooy0604","De Kooy","06","04",4.9666666666666659,14.24]
["De Kooy0605","De Kooy","06","05",4.5133333333333336,13.713333333333333]
["De Kooy0606","De Kooy","06","06",4.4266666666666659,14.333333333333336]
["De Kooy0607","De Kooy","06","07",4.5666666666666682,14.88]
["De Kooy0608","De Kooy","06","08",4.2866666666666671,15.606666666666666]
["De Kooy0609","De Kooy","06","09",4.7799999999999994,15.513333333333334]
["De Kooy0610","De Kooy","06","10",4.26,15.053333333333333]
["De Kooy0611","De Kooy","06","11",4.9533333333333331,14.793333333333331]
["De Kooy0612","De Kooy","06","12",4.9533333333333323,14.653333333333332]
["De Kooy0613","De Kooy","06","13",4.9333333333333327,14.52]
["De Kooy0614","De Kooy","06","14",4.6266666666666669,14.853333333333328]
["De Kooy0615","De Kooy","06","15",5.0066666666666668,14.746666666666666]
["De Kooy0616","De Kooy","06","16",5.2600000000000007,14.566666666666666]
["De Kooy0617","De Kooy","06","17",4.9000000000000004,15.893333333333333]
["De Kooy0618","De Kooy","06","18",4.74,15.979999999999999]
["De Kooy0619","De Kooy","06","19",5.4599999999999991,16.213333333333335]
["De Kooy0620","De Kooy","06","20",5.1999999999999993,16.04]
["De Kooy0621","De Kooy","06","21",4.8999999999999995,15.153333333333334]
["De Kooy0622","De Kooy","06","22",6.1533333333333333,15.559999999999999]
["De Kooy0623","De Kooy","06","23",5.9466666666666663,15.826666666666664]
["De Kooy0624","De Kooy","06","24",5.5133333333333336,15.419999999999996]
["De Kooy0625","De Kooy","06","25",5.0666666666666664,15.460000000000003]
["De Kooy0626","De Kooy","06","26",4.9466666666666672,16.04]
["De Kooy0627","De Kooy","06","27",5.1533333333333333,16.686666666666671]
["De Kooy0628","De Kooy","06","28",5.2399999999999993,16.82]
["De Kooy0629","De Kooy","06","29",5.373333333333334,16.16]
["De Kooy0630","De Kooy","06","30",4.879999999999999,16.28]
["De Kooy0701","De Kooy","07","01",5.34,16.493333333333332]
["De Kooy0702","De Kooy","07","02",4.9666666666666659,17.74666666666667]
["De Kooy0703","De Kooy","07","03",5.0266666666666673,17.546666666666667]
["De Kooy0704","De Kooy","07","04",4.8666666666666663,17.740000000000002]
["De Kooy0705","De Kooy","07","05",4.0733333333333333,17.586666666666662]
["De Kooy0706","De Kooy","07","06",5.1333333333333337,17.013333333333332]
["De Kooy0707","De Kooy","07","07",5.3200000000000012,16.926666666666669]
["De Kooy0708","De Kooy","07","08",5.0199999999999996,16.740000000000002]
["De Kooy0709","De Kooy","07","09",5.426666666666665,16.853333333333335]
["De Kooy0710","De Kooy","07","10",5.546666666666666,17.2]
["De Kooy0711","De Kooy","07","11",5.7799999999999994,16.713333333333331]
["De Kooy0712","De Kooy","07","12",5.1800000000000006,16.313333333333336]
["De Kooy0713","De Kooy","07","13",4.7266666666666675,16.553333333333335]
["De Kooy0714","De Kooy","07","14",5.1400000000000006,17.193333333333332]
["De Kooy0715","De Kooy","07","15",5.3666666666666663,17.373333333333331]
["De Kooy0716","De Kooy","07","16",4.5266666666666673,17.579999999999998]
["De Kooy0717","De Kooy","07","17",5.2466666666666661,17.586666666666666]
["De Kooy0718","De Kooy","07","18",5.9733333333333336,17.433333333333334]
["De Kooy0719","De Kooy","07","19",4.9800000000000004,18.16]
["De Kooy0720","De Kooy","07","20",4.9466666666666663,17.486666666666665]
["De Kooy0721","De Kooy","07","21",4.9266666666666667,17.326666666666664]
["De Kooy0722","De Kooy","07","22",4.76,17.566666666666666]
["De Kooy0723","De Kooy","07","23",4.8,17.933333333333334]
["De Kooy0724","De Kooy","07","24",4.8066666666666666,17.619999999999997]
["De Kooy0725","De Kooy","07","25",4.4333333333333336,18.079999999999998]
["De Kooy0726","De Kooy","07","26",4.2533333333333339,18.333333333333332]
["De Kooy0727","De Kooy","07","27",3.7533333333333325,18.533333333333328]
["De Kooy0728","De Kooy","07","28",4.1066666666666665,18.866666666666667]
["De Kooy0729","De Kooy","07","29",4.206666666666667,18.66]
["De Kooy0730","De Kooy","07","30",4.753333333333333,17.760000000000002]
["De Kooy0731","De Kooy","07","31",4.5600000000000005,17.88]
["De Kooy0801","De Kooy","08","01",4.0399999999999991,18.393333333333334]
["De Kooy0802","De Kooy","08","02",4.206666666666667,18.606666666666669]
["De Kooy0803","De Kooy","08","03",4.4799999999999995,17.780000000000005]
["De Kooy0804","De Kooy","08","04",4.666666666666667,18.040000000000003]
["De Kooy0805","De Kooy","08","05",3.9799999999999991,18.713333333333335]
["De Kooy0806","De Kooy","08","06",4.1999999999999993,18.773333333333337]
["De Kooy0807","De Kooy","08","07",4.2333333333333334,18.206666666666663]
["De Kooy0808","De Kooy","08","08",4.8199999999999994,17.893333333333331]
["De Kooy0809","De Kooy","08","09",4.6933333333333334,17.446666666666665]
["De Kooy0810","De Kooy","08","10",5.1799999999999988,17.293333333333337]
["De Kooy0811","De Kooy","08","11",4.9666666666666659,17.413333333333338]
["De Kooy0812","De Kooy","08","12",4.8733333333333331,17.453333333333333]
["De Kooy0813","De Kooy","08","13",5.48,17.600000000000001]
["De Kooy0814","De Kooy","08","14",4.8666666666666663,18.073333333333331]
["De Kooy0815","De Kooy","08","15",5.0733333333333333,18.293333333333333]
["De Kooy0816","De Kooy","08","16",4.666666666666667,17.946666666666669]
["De Kooy0817","De Kooy","08","17",5.0666666666666664,18.233333333333334]
["De Kooy0818","De Kooy","08","18",5.0133333333333336,18.933333333333334]
["De Kooy0819","De Kooy","08","19",5.206666666666667,18.32]
["De Kooy0820","De Kooy","08","20",4.7733333333333325,17.733333333333334]
["De Kooy0821","De Kooy","08","21",4.7333333333333334,17.433333333333334]
["De Kooy0822","De Kooy","08","22",4.2733333333333343,17.219999999999995]
["De Kooy0823","De Kooy","08","23",3.8933333333333322,17.419999999999998]
["De Kooy0824","De Kooy","08","24",4.28,17.413333333333338]
["De Kooy0825","De Kooy","08","25",4.7666666666666657,17.440000000000001]
["De Kooy0826","De Kooy","08","26",5.3199999999999994,17.333333333333332]
["De Kooy0827","De Kooy","08","27",4.9933333333333332,16.96]
["De Kooy0828","De Kooy","08","28",4.9666666666666659,16.420000000000002]
["De Kooy0829","De Kooy","08","29",5.2333333333333334,16.09333333333333]
["De Kooy0830","De Kooy","08","30",5.2866666666666671,16.653333333333332]
["De Kooy0831","De Kooy","08","31",4.9800000000000004,16.686666666666671]
["De Kooy0901","De Kooy","09","01",4.5733333333333333,16.126666666666669]
["De Kooy0902","De Kooy","09","02",4.92,16.600000000000001]
["De Kooy0903","De Kooy","09","03",5.1000000000000005,16.940000000000001]
["De Kooy0904","De Kooy","09","04",5.12,16.559999999999999]
["De Kooy0905","De Kooy","09","05",4.58,17.073333333333331]
["De Kooy0906","De Kooy","09","06",5.7866666666666671,17.100000000000005]
["De Kooy0907","De Kooy","09","07",5.9133333333333331,16.333333333333332]
["De Kooy0908","De Kooy","09","08",4.9666666666666659,16.239999999999998]
["De Kooy0909","De Kooy","09","09",4.4066666666666663,16.606666666666666]
["De Kooy0910","De Kooy","09","10",5.0666666666666664,16.426666666666666]
["De Kooy0911","De Kooy","09","11",5.4000000000000012,17]
["De Kooy0912","De Kooy","09","12",5.3599999999999985,16.473333333333336]
["De Kooy0913","De Kooy","09","13",5.1066666666666674,15.58]
["De Kooy0914","De Kooy","09","14",6.4066666666666654,16.006666666666668]
["De Kooy0915","De Kooy","09","15",5.3133333333333335,15.413333333333334]
["De Kooy0916","De Kooy","09","16",4.9933333333333341,14.966666666666665]
["De Kooy0917","De Kooy","09","17",4.74,14.966666666666665]
["De Kooy0918","De Kooy","09","18",4.6800000000000006,14.56]
["De Kooy0919","De Kooy","09","19",5.0666666666666673,14.800000000000002]
["De Kooy0920","De Kooy","09","20",5.2933333333333339,15.073333333333332]
["De Kooy0921","De Kooy","09","21",4.9466666666666672,15.086666666666666]
["De Kooy0922","De Kooy","09","22",5.166666666666667,15.32666666666667]
["De Kooy0923","De Kooy","09","23",4.793333333333333,14.620000000000001]
["De Kooy0924","De Kooy","09","24",4.9599999999999991,14.453333333333331]
["De Kooy0925","De Kooy","09","25",4.4266666666666667,14.28]
["De Kooy0926","De Kooy","09","26",4.2733333333333325,14.146666666666667]
["De Kooy0927","De Kooy","09","27",3.8800000000000003,14.093333333333335]
["De Kooy0928","De Kooy","09","28",5.253333333333333,14.713333333333333]
["De Kooy0929","De Kooy","09","29",4.6933333333333334,14.366666666666667]
["De Kooy0930","De Kooy","09","30",5.1133333333333333,14.126666666666669]
["De Kooy1001","De Kooy","10","01",5.4466666666666663,14.02]
["De Kooy1002","De Kooy","10","02",5.5066666666666659,13.84]
["De Kooy1003","De Kooy","10","03",5.8199999999999994,14.400000000000002]
["De Kooy1004","De Kooy","10","04",5.8000000000000007,13.953333333333335]
["De Kooy1005","De Kooy","10","05",5.8266666666666662,13.586666666666668]
["De Kooy1006","De Kooy","10","06",6.2133333333333338,13.200000000000001]
["De Kooy1007","De Kooy","10","07",5.8199999999999994,12.5]
["De Kooy1008","De Kooy","10","08",5.12,12.253333333333334]
["De Kooy1009","De Kooy","10","09",5.5,12.300000000000002]
["De Kooy1010","De Kooy","10","10",6.3133333333333344,12.406666666666666]
["De Kooy1011","De Kooy","10","11",6.5933333333333319,12.306666666666665]
["De Kooy1012","De Kooy","10","12",4.6466666666666665,11.840000000000002]
["De Kooy1013","De Kooy","10","13",4.2399999999999993,11.613333333333333]
["De Kooy1014","De Kooy","10","14",4.6466666666666665,11.339999999999998]
["De Kooy1015","De Kooy","10","15",4.7333333333333334,11.280000000000001]
["De Kooy1016","De Kooy","10","16",6.0533333333333328,11.466666666666669]
["De Kooy1017","De Kooy","10","17",5.1933333333333325,11.08]
["De Kooy1018","De Kooy","10","18",5.4666666666666659,11.213333333333335]
["De Kooy1019","De Kooy","10","19",4.96,11.613333333333333]
["De Kooy1020","De Kooy","10","20",5.6599999999999993,11.2]
["De Kooy1021","De Kooy","10","21",6.9600000000000017,11.573333333333331]
["De Kooy1022","De Kooy","10","22",6.1333333333333346,11.5]
["De Kooy1023","De Kooy","10","23",6.7333333333333334,11.193333333333335]
["De Kooy1024","De Kooy","10","24",6.426666666666665,11.059999999999999]
["De Kooy1025","De Kooy","10","25",7.3133333333333335,11.693333333333333]
["De Kooy1026","De Kooy","10","26",7.2133333333333338,11.386666666666665]
["De Kooy1027","De Kooy","10","27",6.7866666666666662,11]
["De Kooy1028","De Kooy","10","28",6.38,11.046666666666665]
["De Kooy1029","De Kooy","10","29",5.7666666666666666,10.96]
["De Kooy1030","De Kooy","10","30",5.7733333333333343,11.006666666666668]
["De Kooy1031","De Kooy","10","31",5.753333333333333,10.626666666666667]
["De Kooy1101","De Kooy","11","01",5.9,10.66]
["De Kooy1102","De Kooy","11","02",6.1466666666666674,10.666666666666666]
["De Kooy1103","De Kooy","11","03",6.8866666666666667,10.7]
["De Kooy1104","De Kooy","11","04",5.2266666666666657,10.266666666666667]
["De Kooy1105","De Kooy","11","05",5.3400000000000007,9.4933333333333341]
["De Kooy1106","De Kooy","11","06",5.9933333333333341,9.7866666666666653]
["De Kooy1107","De Kooy","11","07",6.1733333333333338,9.3733333333333348]
["De Kooy1108","De Kooy","11","08",6.7266666666666675,8.7066666666666688]
["De Kooy1109","De Kooy","11","09",5.9533333333333331,7.873333333333334]
["De Kooy1110","De Kooy","11","10",5.3733333333333331,8.4466666666666672]
["De Kooy1111","De Kooy","11","11",6.9533333333333331,8.6933333333333316]
["De Kooy1112","De Kooy","11","12",6.5866666666666651,8.7266666666666666]
["De Kooy1113","De Kooy","11","13",5.6066666666666665,8.8733333333333348]
["De Kooy1114","De Kooy","11","14",5.6266666666666669,8.4600000000000009]
["De Kooy1115","De Kooy","11","15",4.8666666666666663,7.6800000000000006]
["De Kooy1116","De Kooy","11","16",4.5533333333333328,7.9200000000000017]
["De Kooy1117","De Kooy","11","17",5.0133333333333328,8.2133333333333329]
["De Kooy1118","De Kooy","11","18",5.3133333333333335,7.7333333333333343]
["De Kooy1119","De Kooy","11","19",4.8000000000000007,7.24]
["De Kooy1120","De Kooy","11","20",5.6400000000000006,7.2866666666666653]
["De Kooy1121","De Kooy","11","21",6.2266666666666657,7.04]
["De Kooy1122","De Kooy","11","22",6.5666666666666673,7.5133333333333336]
["De Kooy1123","De Kooy","11","23",4.9733333333333327,7.4466666666666681]
["De Kooy1124","De Kooy","11","24",5.4733333333333327,7.2799999999999994]
["De Kooy1125","De Kooy","11","25",6.5266666666666673,7.0266666666666664]
["De Kooy1126","De Kooy","11","26",6.0666666666666655,7.0600000000000005]
["De Kooy1127","De Kooy","11","27",5.38,6.8199999999999985]
["De Kooy1128","De Kooy","11","28",5.4666666666666659,6.6266666666666669]
["De Kooy1129","De Kooy","11","29",5.8466666666666667,6.5666666666666673]
["De Kooy1130","De Kooy","11","30",5.1933333333333316,5.9133333333333349]
["De Kooy1201","De Kooy","12","01",6.5266666666666682,5.9933333333333341]
["De Kooy1202","De Kooy","12","02",5.0733333333333333,5.333333333333333]
["De Kooy1203","De Kooy","12","03",5.6,5.8133333333333335]
["De Kooy1204","De Kooy","12","04",6.8533333333333326,6.26]
["De Kooy1205","De Kooy","12","05",7.0333333333333323,6.96]
["De Kooy1206","De Kooy","12","06",6.42,6.620000000000001]
["De Kooy1207","De Kooy","12","07",6.5600000000000005,5.3466666666666676]
["De Kooy1208","De Kooy","12","08",6.1466666666666665,4.746666666666667]
["De Kooy1209","De Kooy","12","09",6.3733333333333331,4.78]
["De Kooy1210","De Kooy","12","10",5.8733333333333322,4.5]
["De Kooy1211","De Kooy","12","11",6.4533333333333331,5.5066666666666659]
["De Kooy1212","De Kooy","12","12",6.0266666666666664,5.0666666666666664]
["De Kooy1213","De Kooy","12","13",6.5,4.333333333333333]
["De Kooy1214","De Kooy","12","14",6.44,3.9533333333333331]
["De Kooy1215","De Kooy","12","15",7.1133333333333333,5.0400000000000009]
["De Kooy1216","De Kooy","12","16",5.9933333333333341,4.4266666666666667]
["De Kooy1217","De Kooy","12","17",5.1466666666666665,4.4000000000000004]
["De Kooy1218","De Kooy","12","18",4.746666666666667,3.8599999999999994]
["De Kooy1219","De Kooy","12","19",5.4333333333333336,3.2133333333333334]
["De Kooy1220","De Kooy","12","20",6.58,3.8600000000000003]
["De Kooy1221","De Kooy","12","21",6.3866666666666667,3.6399999999999997]
["De Kooy1222","De Kooy","12","22",6.0266666666666664,4.3933333333333335]
["De Kooy1223","De Kooy","12","23",6.6,5.0199999999999996]
["De Kooy1224","De Kooy","12","24",7.12,5.8599999999999994]
["De Kooy1225","De Kooy","12","25",6.4266666666666659,5.3666666666666663]
["De Kooy1226","De Kooy","12","26",6.1066666666666665,4.5133333333333328]
["De Kooy1227","De Kooy","12","27",7.5333333333333332,4.206666666666667]
["De Kooy1228","De Kooy","12","28",6.9533333333333331,4.3066666666666666]
["De Kooy1229","De Kooy","12","29",6.2333333333333334,3.9866666666666668]
["De Kooy1230","De Kooy","12","30",6.9066666666666663,3.8866666666666663]
["De Kooy1231","De Kooy","12","31",6.2333333333333343,4.3933333333333326]
["Deelen0101","Deelen","01","01",4.4066666666666663,3.1400000000000006]
["Deelen0102","Deelen","01","02",4.1133333333333333,2.9200000000000004]
["Deelen0103","Deelen","01","03",4.5733333333333333,2.4666666666666668]
["Deelen0104","Deelen","01","04",5.1466666666666656,2.9733333333333336]
["Deelen0105","Deelen","01","05",4.6466666666666665,2.7666666666666666]
["Deelen0106","Deelen","01","06",4.1933333333333334,3.3800000000000003]
["Deelen0107","Deelen","01","07",4.5266666666666673,3.953333333333334]
["Deelen0108","Deelen","01","08",4.9866666666666672,3.52]
["Deelen0109","Deelen","01","09",4.4866666666666672,2.4266666666666667]
["Deelen0110","Deelen","01","10",4.1733333333333338,2.4799999999999995]
["Deelen0111","Deelen","01","11",4.8133333333333326,3.2666666666666666]
["Deelen0112","Deelen","01","12",4.66,3.1133333333333328]
["Deelen0113","Deelen","01","13",4.9333333333333336,3.5333333333333328]
["Deelen0114","Deelen","01","14",3.8800000000000008,2.98]
["Deelen0115","Deelen","01","15",4.4399999999999995,2.4533333333333331]
["Deelen0116","Deelen","01","16",4.38,2.5866666666666673]
["Deelen0117","Deelen","01","17",4.7333333333333334,3.52]
["Deelen0118","Deelen","01","18",5.0933333333333337,3.7733333333333334]
["Deelen0119","Deelen","01","19",4.6999999999999993,4.3466666666666676]
["Deelen0120","Deelen","01","20",5.2800000000000011,4.3600000000000003]
["Deelen0121","Deelen","01","21",4.6933333333333325,3.8400000000000007]
["Deelen0122","Deelen","01","22",4.3,2.6733333333333329]
["Deelen0123","Deelen","01","23",4.0999999999999996,1.8333333333333335]
["Deelen0124","Deelen","01","24",3.3066666666666662,1.5133333333333332]
["Deelen0125","Deelen","01","25",3.9333333333333327,1.1066666666666665]
["Deelen0126","Deelen","01","26",4.9466666666666663,1.7866666666666668]
["Deelen0127","Deelen","01","27",4.3533333333333335,2.4533333333333327]
["Deelen0128","Deelen","01","28",4.8066666666666675,2.68]
["Deelen0129","Deelen","01","29",4.6066666666666665,2.5999999999999996]
["Deelen0130","Deelen","01","30",4.2399999999999993,2.8533333333333331]
["Deelen0131","Deelen","01","31",5.3533333333333344,2.3533333333333331]
["Deelen0201","Deelen","02","01",5.4066666666666672,2.5933333333333333]
["Deelen0202","Deelen","02","02",5.0600000000000005,3.0333333333333332]
["Deelen0203","Deelen","02","03",3.9933333333333332,3.1133333333333337]
["Deelen0204","Deelen","02","04",4.7533333333333339,3.9333333333333327]
["Deelen0205","Deelen","02","05",5.5066666666666659,4.74]
["Deelen0206","Deelen","02","06",4.5133333333333336,4.333333333333333]
["Deelen0207","Deelen","02","07",4.7199999999999989,3.4133333333333327]
["Deelen0208","Deelen","02","08",4.833333333333333,3.2666666666666666]
["Deelen0209","Deelen","02","09",4.5133333333333336,2.6]
["Deelen0210","Deelen","02","10",4.54,2.6066666666666669]
["Deelen0211","Deelen","02","11",4.2466666666666661,3.1999999999999997]
["Deelen0212","Deelen","02","12",4.6799999999999988,3.18]
["Deelen0213","Deelen","02","13",3.626666666666666,2.8866666666666663]
["Deelen0214","Deelen","02","14",3.9199999999999995,2.44]
["Deelen0215","Deelen","02","15",4.1533333333333333,3.0000000000000004]
["Deelen0216","Deelen","02","16",3.8666666666666663,2.8066666666666666]
["Deelen0217","Deelen","02","17",3.32,2.36]
["Deelen0218","Deelen","02","18",3.3399999999999994,2.546666666666666]
["Deelen0219","Deelen","02","19",4.1733333333333338,2.7866666666666666]
["Deelen0220","Deelen","02","20",4.366666666666668,2.5866666666666664]
["Deelen0221","Deelen","02","21",4.4000000000000004,2.7133333333333329]
["Deelen0222","Deelen","02","22",5.1333333333333337,3.4133333333333331]
["Deelen0223","Deelen","02","23",4.4866666666666672,3.4133333333333336]
["Deelen0224","Deelen","02","24",4.28,4.0533333333333328]
["Deelen0225","Deelen","02","25",4.1733333333333329,4.0199999999999996]
["Deelen0226","Deelen","02","26",4.7533333333333321,4.746666666666667]
["Deelen0227","Deelen","02","27",4.6933333333333334,3.9333333333333331]
["Deelen0228","Deelen","02","28",3.9733333333333336,4.366666666666668]
["Deelen0229","Deelen","02","29",4.7,5.1749999999999998]
["Deelen0301","Deelen","03","01",4.3599999999999994,4.04]
["Deelen0302","Deelen","03","02",4.1800000000000006,3.5799999999999996]
["Deelen0303","Deelen","03","03",3.7400000000000007,2.8933333333333335]
["Deelen0304","Deelen","03","04",3.8000000000000003,3.0333333333333332]
["Deelen0305","Deelen","03","05",3.5733333333333328,3.8]
["Deelen0306","Deelen","03","06",4.7200000000000006,4.4333333333333336]
["Deelen0307","Deelen","03","07",4.2733333333333325,5.0866666666666678]
["Deelen0308","Deelen","03","08",4.6066666666666665,5.8266666666666671]
["Deelen0309","Deelen","03","09",4.9733333333333336,6.253333333333333]
["Deelen0310","Deelen","03","10",4.7066666666666661,5.4066666666666672]
["Deelen0311","Deelen","03","11",5.0199999999999996,5.6733333333333329]
["Deelen0312","Deelen","03","12",3.9599999999999995,5.38]
["Deelen0313","Deelen","03","13",3.5799999999999996,5.2266666666666675]
["Deelen0314","Deelen","03","14",3.86,5.166666666666667]
["Deelen0315","Deelen","03","15",4.4000000000000004,6.0733333333333333]
["Deelen0316","Deelen","03","16",4.2866666666666662,7.4066666666666672]
["Deelen0317","Deelen","03","17",4.4333333333333345,6.9733333333333318]
["Deelen0318","Deelen","03","18",4.1733333333333338,6.3000000000000007]
["Deelen0319","Deelen","03","19",4.1333333333333337,5.666666666666667]
["Deelen0320","Deelen","03","20",3.96,5.9000000000000021]
["Deelen0321","Deelen","03","21",3.7733333333333334,5.3133333333333326]
["Deelen0322","Deelen","03","22",3.9799999999999995,5.6666666666666661]
["Deelen0323","Deelen","03","23",3.7,5.76]
["Deelen0324","Deelen","03","24",3.7133333333333334,6.4599999999999991]
["Deelen0325","Deelen","03","25",3.8733333333333331,6.6266666666666669]
["Deelen0326","Deelen","03","26",3.3533333333333331,6.3199999999999994]
["Deelen0327","Deelen","03","27",3.8266666666666667,6.76]
["Deelen0328","Deelen","03","28",4.1733333333333329,7.3466666666666667]
["Deelen0329","Deelen","03","29",3.4466666666666663,7.38]
["Deelen0330","Deelen","03","30",3.8533333333333331,8.3333333333333339]
["Deelen0331","Deelen","03","31",4.1999999999999993,8.3866666666666667]
["Deelen0401","Deelen","04","01",4.2733333333333343,9.0133333333333319]
["Deelen0402","Deelen","04","02",4.58,10.4]
["Deelen0403","Deelen","04","03",4.4066666666666663,9.8733333333333331]
["Deelen0404","Deelen","04","04",4.3266666666666671,8.3533333333333317]
["Deelen0405","Deelen","04","05",4.5733333333333341,7.0733333333333333]
["Deelen0406","Deelen","04","06",4.1466666666666665,7.8333333333333321]
["Deelen0407","Deelen","04","07",3.6133333333333324,7.5133333333333336]
["Deelen0408","Deelen","04","08",3.7066666666666661,6.4066666666666672]
["Deelen0409","Deelen","04","09",3.5133333333333336,7.0533333333333328]
["Deelen0410","Deelen","04","10",3.3999999999999995,7.746666666666667]
["Deelen0411","Deelen","04","11",3.3066666666666662,8.2533333333333339]
["Deelen0412","Deelen","04","12",3.6733333333333333,8.1533333333333342]
["Deelen0413","Deelen","04","13",4,8.9]
["Deelen0414","Deelen","04","14",3.5599999999999996,9.4]
["Deelen0415","Deelen","04","15",3.8066666666666662,10.126666666666665]
["Deelen0416","Deelen","04","16",3.4399999999999995,9.8866666666666649]
["Deelen0417","Deelen","04","17",3.773333333333333,10.193333333333332]
["Deelen0418","Deelen","04","18",4.8466666666666667,9.5533333333333328]
["Deelen0419","Deelen","04","19",3.9866666666666659,9.1133333333333333]
["Deelen0420","Deelen","04","20",3.5533333333333332,9.793333333333333]
["Deelen0421","Deelen","04","21",3.3200000000000003,10.933333333333332]
["Deelen0422","Deelen","04","22",3.0799999999999996,11.06]
["Deelen0423","Deelen","04","23",2.88,11.573333333333332]
["Deelen0424","Deelen","04","24",3.0933333333333333,13.379999999999997]
["Deelen0425","Deelen","04","25",3.4666666666666668,14.12666666666667]
["Deelen0426","Deelen","04","26",3.5600000000000005,12.826666666666666]
["Deelen0427","Deelen","04","27",4.1199999999999992,12.433333333333334]
["Deelen0428","Deelen","04","28",3.6600000000000006,12.533333333333335]
["Deelen0429","Deelen","04","29",4.0666666666666664,12.253333333333332]
["Deelen0430","Deelen","04","30",3.9200000000000013,12.493333333333334]
["Deelen0501","Deelen","05","01",4.2,12.386666666666665]
["Deelen0502","Deelen","05","02",3.9466666666666663,11.933333333333334]
["Deelen0503","Deelen","05","03",3.5266666666666668,11.806666666666667]
["Deelen0504","Deelen","05","04",3.9466666666666672,11.453333333333337]
["Deelen0505","Deelen","05","05",3.9666666666666668,12.086666666666668]
["Deelen0506","Deelen","05","06",3.8866666666666663,12.946666666666669]
["Deelen0507","Deelen","05","07",3.9399999999999995,13.126666666666665]
["Deelen0508","Deelen","05","08",4.0733333333333324,13.753333333333332]
["Deelen0509","Deelen","05","09",3.4466666666666663,14.106666666666666]
["Deelen0510","Deelen","05","10",3.7733333333333334,14.360000000000001]
["Deelen0511","Deelen","05","11",4.4399999999999995,13.459999999999999]
["Deelen0512","Deelen","05","12",4.0599999999999996,12.479999999999999]
["Deelen0513","Deelen","05","13",3.86,13.319999999999997]
["Deelen0514","Deelen","05","14",3.6933333333333334,12.493333333333334]
["Deelen0515","Deelen","05","15",3.2266666666666666,12.453333333333335]
["Deelen0516","Deelen","05","16",3.6333333333333337,12.826666666666664]
["Deelen0517","Deelen","05","17",3.3066666666666662,12.326666666666664]
["Deelen0518","Deelen","05","18",3.6666666666666665,12.746666666666666]
["Deelen0519","Deelen","05","19",3.7866666666666662,13.046666666666665]
["Deelen0520","Deelen","05","20",3.5466666666666669,13.926666666666666]
["Deelen0521","Deelen","05","21",3.5933333333333337,14.26]
["Deelen0522","Deelen","05","22",3.88,14.033333333333331]
["Deelen0523","Deelen","05","23",3.3199999999999994,14.080000000000002]
["Deelen0524","Deelen","05","24",3.9266666666666667,14.620000000000001]
["Deelen0525","Deelen","05","25",3.7133333333333329,14.42]
["Deelen0526","Deelen","05","26",4.1933333333333342,14.046666666666669]
["Deelen0527","Deelen","05","27",3.6333333333333337,14.626666666666665]
["Deelen0528","Deelen","05","28",4.0733333333333333,14.933333333333334]
["Deelen0529","Deelen","05","29",4.0199999999999996,13.973333333333334]
["Deelen0530","Deelen","05","30",3.1133333333333337,14.34]
["Deelen0531","Deelen","05","31",3.5066666666666659,13.873333333333331]
["Deelen0601","Deelen","06","01",3.2066666666666666,14.393333333333334]
["Deelen0602","Deelen","06","02",3.6733333333333333,15.586666666666668]
["Deelen0603","Deelen","06","03",3.5533333333333332,15.273333333333335]
["Deelen0604","Deelen","06","04",3.6933333333333329,15.360000000000001]
["Deelen0605","Deelen","06","05",3.1666666666666665,14.753333333333334]
["Deelen0606","Deelen","06","06",2.9533333333333336,15.546666666666665]
["Deelen0607","Deelen","06","07",3.2666666666666671,16.159999999999997]
["Deelen0608","Deelen","06","08",3.1666666666666665,16.746666666666666]
["Deelen0609","Deelen","06","09",3.2933333333333334,16.7]
["Deelen0610","Deelen","06","10",2.9666666666666668,16.28]
["Deelen0611","Deelen","06","11",3.4599999999999995,15.426666666666668]
["Deelen0612","Deelen","06","12",3.2466666666666666,15.106666666666667]
["Deelen0613","Deelen","06","13",2.9599999999999995,15.24]
["Deelen0614","Deelen","06","14",3.12,15.873333333333337]
["Deelen0615","Deelen","06","15",3.5399999999999996,15.640000000000002]
["Deelen0616","Deelen","06","16",3.4,15.093333333333335]
["Deelen0617","Deelen","06","17",3.4933333333333336,16.873333333333331]
["Deelen0618","Deelen","06","18",3.4666666666666668,17.38666666666667]
["Deelen0619","Deelen","06","19",3.5333333333333328,16.946666666666669]
["Deelen0620","Deelen","06","20",3.4466666666666668,17.100000000000001]
["Deelen0621","Deelen","06","21",3.4399999999999995,15.96]
["Deelen0622","Deelen","06","22",3.7266666666666666,15.826666666666666]
["Deelen0623","Deelen","06","23",4.0733333333333333,16.266666666666666]
["Deelen0624","Deelen","06","24",3.726666666666667,16.506666666666668]
["Deelen0625","Deelen","06","25",3.6666666666666661,15.780000000000001]
["Deelen0626","Deelen","06","26",3.2133333333333334,16.426666666666666]
["Deelen0627","Deelen","06","27",3.5200000000000005,17.353333333333332]
["Deelen0628","Deelen","06","28",3.3800000000000003,17.48]
["Deelen0629","Deelen","06","29",3.2800000000000002,16.733333333333331]
["Deelen0630","Deelen","06","30",3.0066666666666668,17.086666666666662]
["Deelen0701","Deelen","07","01",3.5000000000000004,17.033333333333335]
["Deelen0702","Deelen","07","02",3.3466666666666662,18.173333333333336]
["Deelen0703","Deelen","07","03",3.6333333333333329,18.186666666666664]
["Deelen0704","Deelen","07","04",3.4266666666666672,18.493333333333332]
["Deelen0705","Deelen","07","05",3.1533333333333338,18.433333333333334]
["Deelen0706","Deelen","07","06",3.2866666666666666,17.673333333333336]
["Deelen0707","Deelen","07","07",3.6533333333333333,17.253333333333334]
["Deelen0708","Deelen","07","08",3.52,17.059999999999999]
["Deelen0709","Deelen","07","09",3.7133333333333334,17.180000000000003]
["Deelen0710","Deelen","07","10",3.56,17.426666666666666]
["Deelen0711","Deelen","07","11",3.9933333333333332,16.90666666666667]
["Deelen0712","Deelen","07","12",3.52,16.673333333333332]
["Deelen0713","Deelen","07","13",3.3133333333333335,16.873333333333328]
["Deelen0714","Deelen","07","14",3.8733333333333326,17.36]
["Deelen0715","Deelen","07","15",3.7199999999999998,18.306666666666668]
["Deelen0716","Deelen","07","16",3.46,18.646666666666665]
["Deelen0717","Deelen","07","17",3.5399999999999996,18.126666666666669]
["Deelen0718","Deelen","07","18",3.9333333333333327,18.286666666666669]
["Deelen0719","Deelen","07","19",3.5200000000000005,18.766666666666666]
["Deelen0720","Deelen","07","20",3.22,17.90666666666667]
["Deelen0721","Deelen","07","21",3.2333333333333334,17.746666666666663]
["Deelen0722","Deelen","07","22",2.9266666666666667,18.293333333333333]
["Deelen0723","Deelen","07","23",3.0733333333333328,18.113333333333333]
["Deelen0724","Deelen","07","24",3.473333333333334,18.033333333333339]
["Deelen0725","Deelen","07","25",3.026666666666666,18.466666666666665]
["Deelen0726","Deelen","07","26",2.8266666666666667,18.893333333333334]
["Deelen0727","Deelen","07","27",2.6399999999999997,19.673333333333332]
["Deelen0728","Deelen","07","28",2.7133333333333334,19.379999999999995]
["Deelen0729","Deelen","07","29",2.7999999999999994,19.14]
["Deelen0730","Deelen","07","30",3.2666666666666662,18.12]
["Deelen0731","Deelen","07","31",2.6866666666666665,17.966666666666665]
["Deelen0801","Deelen","08","01",2.7399999999999998,18.77333333333333]
["Deelen0802","Deelen","08","02",2.8333333333333339,18.839999999999996]
["Deelen0803","Deelen","08","03",2.7133333333333329,18.019999999999996]
["Deelen0804","Deelen","08","04",2.9199999999999995,18.48]
["Deelen0805","Deelen","08","05",2.88,19]
["Deelen0806","Deelen","08","06",3.0933333333333337,19.12]
["Deelen0807","Deelen","08","07",3.0133333333333328,18.260000000000002]
["Deelen0808","Deelen","08","08",3.4,17.626666666666665]
["Deelen0809","Deelen","08","09",3.2800000000000007,17.36]
["Deelen0810","Deelen","08","10",3.48,17.160000000000004]
["Deelen0811","Deelen","08","11",3.2466666666666666,17.279999999999998]
["Deelen0812","Deelen","08","12",3.2333333333333338,17.2]
["Deelen0813","Deelen","08","13",3.566666666666666,17.166666666666664]
["Deelen0814","Deelen","08","14",2.9866666666666664,17.606666666666666]
["Deelen0815","Deelen","08","15",3.4599999999999995,18.133333333333329]
["Deelen0816","Deelen","08","16",2.813333333333333,17.739999999999998]
["Deelen0817","Deelen","08","17",3.3399999999999994,17.773333333333333]
["Deelen0818","Deelen","08","18",3.5533333333333328,18.673333333333336]
["Deelen0819","Deelen","08","19",3.6666666666666665,18.553333333333335]
["Deelen0820","Deelen","08","20",2.9666666666666672,17.626666666666665]
["Deelen0821","Deelen","08","21",2.9066666666666663,17.146666666666668]
["Deelen0822","Deelen","08","22",2.8933333333333331,16.733333333333334]
["Deelen0823","Deelen","08","23",3.0733333333333328,17.213333333333331]
["Deelen0824","Deelen","08","24",3.0333333333333332,17.259999999999998]
["Deelen0825","Deelen","08","25",2.9866666666666664,17.153333333333332]
["Deelen0826","Deelen","08","26",3.7133333333333329,17.059999999999995]
["Deelen0827","Deelen","08","27",3.2133333333333329,16.033333333333335]
["Deelen0828","Deelen","08","28",3,15.606666666666671]
["Deelen0829","Deelen","08","29",3.0066666666666664,15.019999999999998]
["Deelen0830","Deelen","08","30",3.1866666666666665,15.046666666666665]
["Deelen0831","Deelen","08","31",3.2333333333333329,15.553333333333333]
["Deelen0901","Deelen","09","01",2.8333333333333335,14.82666666666667]
["Deelen0902","Deelen","09","02",3.2266666666666661,15.753333333333336]
["Deelen0903","Deelen","09","03",3.4866666666666664,16.006666666666668]
["Deelen0904","Deelen","09","04",3.246666666666667,16.113333333333333]
["Deelen0905","Deelen","09","05",3.1466666666666665,16.46]
["Deelen0906","Deelen","09","06",3.6133333333333324,16.706666666666663]
["Deelen0907","Deelen","09","07",3.8199999999999994,15.873333333333333]
["Deelen0908","Deelen","09","08",3.2266666666666666,15.74]
["Deelen0909","Deelen","09","09",3.0933333333333333,16.046666666666667]
["Deelen0910","Deelen","09","10",3.4266666666666672,16.053333333333335]
["Deelen0911","Deelen","09","11",3.4200000000000004,16.16]
["Deelen0912","Deelen","09","12",3.3866666666666663,15.366666666666667]
["Deelen0913","Deelen","09","13",3.22,14.66]
["Deelen0914","Deelen","09","14",3.9466666666666663,14.533333333333333]
["Deelen0915","Deelen","09","15",3.4933333333333332,14.153333333333334]
["Deelen0916","Deelen","09","16",3.2733333333333334,13.953333333333335]
["Deelen0917","Deelen","09","17",3.0133333333333332,13.473333333333334]
["Deelen0918","Deelen","09","18",2.726666666666667,13.453333333333335]
["Deelen0919","Deelen","09","19",3.3666666666666671,13.44]
["Deelen0920","Deelen","09","20",3.1933333333333334,13.826666666666666]
["Deelen0921","Deelen","09","21",2.9600000000000004,13.859999999999998]
["Deelen0922","Deelen","09","22",3.4266666666666667,14.186666666666667]
["Deelen0923","Deelen","09","23",3.1133333333333324,13.673333333333336]
["Deelen0924","Deelen","09","24",3.253333333333333,13.306666666666667]
["Deelen0925","Deelen","09","25",2.9933333333333332,13.013333333333334]
["Deelen0926","Deelen","09","26",2.813333333333333,13.02]
["Deelen0927","Deelen","09","27",2.6733333333333333,12.98666666666667]
["Deelen0928","Deelen","09","28",3.12,13.639999999999999]
["Deelen0929","Deelen","09","29",3.3933333333333335,13.553333333333335]
["Deelen0930","Deelen","09","30",3.3266666666666667,13.073333333333334]
["Deelen1001","Deelen","10","01",3.52,13.200000000000001]
["Deelen1002","Deelen","10","02",3.6333333333333329,13.013333333333337]
["Deelen1003","Deelen","10","03",3.7533333333333334,13.520000000000003]
["Deelen1004","Deelen","10","04",3.8266666666666658,12.820000000000002]
["Deelen1005","Deelen","10","05",3.7066666666666661,12.540000000000001]
["Deelen1006","Deelen","10","06",3.9066666666666672,12.126666666666669]
["Deelen1007","Deelen","10","07",3.5200000000000005,11.32]
["Deelen1008","Deelen","10","08",3.1866666666666665,10.746666666666668]
["Deelen1009","Deelen","10","09",3.4200000000000004,11]
["Deelen1010","Deelen","10","10",4.2199999999999989,11.573333333333332]
["Deelen1011","Deelen","10","11",4.1133333333333333,11.020000000000001]
["Deelen1012","Deelen","10","12",3.4200000000000004,10.66]
["Deelen1013","Deelen","10","13",3.1,10.773333333333333]
["Deelen1014","Deelen","10","14",3.2866666666666666,10.393333333333333]
["Deelen1015","Deelen","10","15",3.5266666666666664,10.233333333333333]
["Deelen1016","Deelen","10","16",4.2133333333333338,10.153333333333332]
["Deelen1017","Deelen","10","17",3.8666666666666667,9.6999999999999993]
["Deelen1018","Deelen","10","18",3.6933333333333334,9.8866666666666667]
["Deelen1019","Deelen","10","19",3.5599999999999996,10.26]
["Deelen1020","Deelen","10","20",4.0066666666666668,10.633333333333335]
["Deelen1021","Deelen","10","21",4.333333333333333,10.713333333333333]
["Deelen1022","Deelen","10","22",4.1466666666666665,10.620000000000001]
["Deelen1023","Deelen","10","23",4.5333333333333323,10.366666666666669]
["Deelen1024","Deelen","10","24",4.4400000000000004,9.8466666666666658]
["Deelen1025","Deelen","10","25",4.7133333333333329,10.533333333333333]
["Deelen1026","Deelen","10","26",4.5999999999999996,10.419999999999998]
["Deelen1027","Deelen","10","27",4.5333333333333332,9.5266666666666673]
["Deelen1028","Deelen","10","28",4.1333333333333337,9.6733333333333338]
["Deelen1029","Deelen","10","29",3.9399999999999995,9.7733333333333334]
["Deelen1030","Deelen","10","30",3.726666666666667,9.8000000000000025]
["Deelen1031","Deelen","10","31",4.0733333333333324,9.7133333333333365]
["Deelen1101","Deelen","11","01",4.1066666666666665,9.2866666666666653]
["Deelen1102","Deelen","11","02",4.12,9.7066666666666688]
["Deelen1103","Deelen","11","03",4.6333333333333337,9.8866666666666667]
["Deelen1104","Deelen","11","04",3.7333333333333338,9.1266666666666669]
["Deelen1105","Deelen","11","05",3.8,8.2733333333333334]
["Deelen1106","Deelen","11","06",3.98,8.4199999999999982]
["Deelen1107","Deelen","11","07",4.0133333333333336,7.8866666666666676]
["Deelen1108","Deelen","11","08",4.5466666666666669,7.54]
["Deelen1109","Deelen","11","09",4.1999999999999993,6.666666666666667]
["Deelen1110","Deelen","11","10",3.8733333333333326,6.6466666666666656]
["Deelen1111","Deelen","11","11",4.746666666666667,6.96]
["Deelen1112","Deelen","11","12",4.3533333333333335,7.2066666666666643]
["Deelen1113","Deelen","11","13",3.3933333333333331,7.0400000000000018]
["Deelen1114","Deelen","11","14",3.8200000000000003,6.8933333333333326]
["Deelen1115","Deelen","11","15",3.3533333333333335,6.0333333333333323]
["Deelen1116","Deelen","11","16",3.0200000000000005,6.206666666666667]
["Deelen1117","Deelen","11","17",3.32,6.3266666666666671]
["Deelen1118","Deelen","11","18",3.5866666666666669,6.3466666666666667]
["Deelen1119","Deelen","11","19",3.38,6.1266666666666669]
["Deelen1120","Deelen","11","20",3.7999999999999994,6.1533333333333333]
["Deelen1121","Deelen","11","21",4.2600000000000007,5.7800000000000011]
["Deelen1122","Deelen","11","22",4.3533333333333335,6.3]
["Deelen1123","Deelen","11","23",3.6666666666666665,6.2733333333333317]
["Deelen1124","Deelen","11","24",3.4066666666666667,5.4666666666666668]
["Deelen1125","Deelen","11","25",4.4866666666666664,5.6866666666666656]
["Deelen1126","Deelen","11","26",4.0266666666666664,5.0400000000000009]
["Deelen1127","Deelen","11","27",3.5866666666666669,5.2600000000000007]
["Deelen1128","Deelen","11","28",3.4733333333333336,5.2733333333333325]
["Deelen1129","Deelen","11","29",3.933333333333334,5.246666666666667]
["Deelen1130","Deelen","11","30",3.4666666666666668,4.4933333333333341]
["Deelen1201","Deelen","12","01",4.5533333333333355,5.1733333333333329]
["Deelen1202","Deelen","12","02",3.8199999999999994,4.16]
["Deelen1203","Deelen","12","03",3.9,4.0866666666666669]
["Deelen1204","Deelen","12","04",4.5600000000000005,4.2666666666666666]
["Deelen1205","Deelen","12","05",4.72,5.5666666666666673]
["Deelen1206","Deelen","12","06",4.38,4.92]
["Deelen1207","Deelen","12","07",4.7399999999999984,3.7666666666666657]
["Deelen1208","Deelen","12","08",4.38,3.2333333333333329]
["Deelen1209","Deelen","12","09",4.1066666666666665,2.7866666666666666]
["Deelen1210","Deelen","12","10",3.473333333333334,2.1666666666666665]
["Deelen1211","Deelen","12","11",4.2666666666666666,3.3266666666666667]
["Deelen1212","Deelen","12","12",4.2266666666666666,3.606666666666666]
["Deelen1213","Deelen","12","13",4.746666666666667,2.8066666666666666]
["Deelen1214","Deelen","12","14",4.3599999999999994,2.2866666666666671]
["Deelen1215","Deelen","12","15",4.5666666666666664,3.2266666666666666]
["Deelen1216","Deelen","12","16",4.2466666666666661,2.8466666666666667]
["Deelen1217","Deelen","12","17",3.4866666666666664,2.2000000000000002]
["Deelen1218","Deelen","12","18",3.18,1.6933333333333331]
["Deelen1219","Deelen","12","19",3.3333333333333335,1.0866666666666669]
["Deelen1220","Deelen","12","20",4.0133333333333336,1.3266666666666667]
["Deelen1221","Deelen","12","21",4.08,2.1733333333333333]
["Deelen1222","Deelen","12","22",4.3599999999999994,3.4399999999999995]
["Deelen1223","Deelen","12","23",4.5066666666666659,3.7333333333333329]
["Deelen1224","Deelen","12","24",5.1799999999999988,4.46]
["Deelen1225","Deelen","12","25",4.5533333333333337,3.9866666666666672]
["Deelen1226","Deelen","12","26",4.04,2.8333333333333335]
["Deelen1227","Deelen","12","27",4.96,2.6466666666666674]
["Deelen1228","Deelen","12","28",4.8733333333333331,2.7399999999999998]
["Deelen1229","Deelen","12","29",4.3066666666666666,2.5266666666666664]
["Deelen1230","Deelen","12","30",4.506666666666665,2.2133333333333334]
["Deelen1231","Deelen","12","31",4.1866666666666665,2.44]
["Eindhoven0101","Eindhoven","01","01",4.4666666666666659,3.96]
["Eindhoven0102","Eindhoven","01","02",4.2266666666666666,3.3600000000000003]
["Eindhoven0103","Eindhoven","01","03",4.54,2.9733333333333336]
["Eindhoven0104","Eindhoven","01","04",5.2600000000000007,3.4533333333333336]
["Eindhoven0105","Eindhoven","01","05",4.6333333333333337,3.2199999999999993]
["Eindhoven0106","Eindhoven","01","06",4.2333333333333325,3.7866666666666671]
["Eindhoven0107","Eindhoven","01","07",4.4933333333333341,4.38]
["Eindhoven0108","Eindhoven","01","08",4.7600000000000007,3.9399999999999991]
["Eindhoven0109","Eindhoven","01","09",4.4666666666666668,2.873333333333334]
["Eindhoven0110","Eindhoven","01","10",3.9533333333333331,2.7666666666666666]
["Eindhoven0111","Eindhoven","01","11",4.7533333333333321,3.5066666666666668]
["Eindhoven0112","Eindhoven","01","12",4.6533333333333333,3.5066666666666668]
["Eindhoven0113","Eindhoven","01","13",4.8266666666666662,4.0066666666666668]
["Eindhoven0114","Eindhoven","01","14",3.92,3.5066666666666668]
["Eindhoven0115","Eindhoven","01","15",4.2266666666666666,2.8600000000000003]
["Eindhoven0116","Eindhoven","01","16",4.0066666666666659,2.9933333333333332]
["Eindhoven0117","Eindhoven","01","17",4.4733333333333327,3.9466666666666663]
["Eindhoven0118","Eindhoven","01","18",4.919999999999999,4.4133333333333331]
["Eindhoven0119","Eindhoven","01","19",4.7200000000000006,5.1400000000000006]
["Eindhoven0120","Eindhoven","01","20",5.3266666666666662,5.1333333333333337]
["Eindhoven0121","Eindhoven","01","21",4.5666666666666664,4.4933333333333341]
["Eindhoven0122","Eindhoven","01","22",4.1866666666666665,3.4733333333333332]
["Eindhoven0123","Eindhoven","01","23",4.0599999999999996,2.6599999999999997]
["Eindhoven0124","Eindhoven","01","24",3.2933333333333334,1.993333333333333]
["Eindhoven0125","Eindhoven","01","25",3.7666666666666662,1.6600000000000001]
["Eindhoven0126","Eindhoven","01","26",4.8066666666666675,2.1533333333333333]
["Eindhoven0127","Eindhoven","01","27",4.253333333333333,2.56]
["Eindhoven0128","Eindhoven","01","28",4.9133333333333331,2.9733333333333336]
["Eindhoven0129","Eindhoven","01","29",4.6333333333333337,3.22]
["Eindhoven0130","Eindhoven","01","30",4.1466666666666665,3.3866666666666658]
["Eindhoven0131","Eindhoven","01","31",5.379999999999999,3.1733333333333329]
["Eindhoven0201","Eindhoven","02","01",5.1400000000000006,2.9733333333333336]
["Eindhoven0202","Eindhoven","02","02",4.8066666666666666,3.4266666666666667]
["Eindhoven0203","Eindhoven","02","03",3.8866666666666658,3.6199999999999997]
["Eindhoven0204","Eindhoven","02","04",4.7666666666666666,4.7733333333333343]
["Eindhoven0205","Eindhoven","02","05",5.0933333333333337,5.166666666666667]
["Eindhoven0206","Eindhoven","02","06",4.4066666666666663,4.8533333333333344]
["Eindhoven0207","Eindhoven","02","07",4.7533333333333339,3.8600000000000003]
["Eindhoven0208","Eindhoven","02","08",4.9466666666666672,3.9466666666666672]
["Eindhoven0209","Eindhoven","02","09",4.3600000000000003,3.1466666666666665]
["Eindhoven0210","Eindhoven","02","10",4.4133333333333322,3.2400000000000007]
["Eindhoven0211","Eindhoven","02","11",4.4266666666666659,3.9066666666666663]
["Eindhoven0212","Eindhoven","02","12",4.5933333333333328,3.6933333333333334]
["Eindhoven0213","Eindhoven","02","13",3.6866666666666665,3.2199999999999998]
["Eindhoven0214","Eindhoven","02","14",3.8400000000000003,2.9]
["Eindhoven0215","Eindhoven","02","15",4.3199999999999994,3.6999999999999997]
["Eindhoven0216","Eindhoven","02","16",3.8466666666666662,3.4333333333333327]
["Eindhoven0217","Eindhoven","02","17",3.3933333333333331,3.0399999999999996]
["Eindhoven0218","Eindhoven","02","18",3.2800000000000002,2.8866666666666663]
["Eindhoven0219","Eindhoven","02","19",4.0333333333333332,3.4333333333333327]
["Eindhoven0220","Eindhoven","02","20",4.12,3.3333333333333335]
["Eindhoven0221","Eindhoven","02","21",4.22,3.2866666666666671]
["Eindhoven0222","Eindhoven","02","22",4.9333333333333327,4.0200000000000005]
["Eindhoven0223","Eindhoven","02","23",4.4066666666666663,3.9133333333333336]
["Eindhoven0224","Eindhoven","02","24",4.0866666666666669,4.76]
["Eindhoven0225","Eindhoven","02","25",4.34,4.8666666666666663]
["Eindhoven0226","Eindhoven","02","26",4.72,4.9933333333333332]
["Eindhoven0227","Eindhoven","02","27",4.7933333333333339,4.4000000000000004]
["Eindhoven0228","Eindhoven","02","28",4.2333333333333334,4.7800000000000011]
["Eindhoven0229","Eindhoven","02","29",4.6749999999999998,5.6749999999999998]
["Eindhoven0301","Eindhoven","03","01",4.4333333333333336,4.633333333333332]
["Eindhoven0302","Eindhoven","03","02",3.9866666666666659,4.1733333333333338]
["Eindhoven0303","Eindhoven","03","03",4,3.686666666666667]
["Eindhoven0304","Eindhoven","03","04",3.5066666666666668,3.7466666666666666]
["Eindhoven0305","Eindhoven","03","05",3.5266666666666668,4.1333333333333337]
["Eindhoven0306","Eindhoven","03","06",4.5599999999999996,4.7799999999999994]
["Eindhoven0307","Eindhoven","03","07",4.1866666666666665,5.9999999999999991]
["Eindhoven0308","Eindhoven","03","08",4.3,6.6466666666666665]
["Eindhoven0309","Eindhoven","03","09",5.08,6.9066666666666663]
["Eindhoven0310","Eindhoven","03","10",4.9000000000000004,6.06]
["Eindhoven0311","Eindhoven","03","11",4.8133333333333335,6.3066666666666658]
["Eindhoven0312","Eindhoven","03","12",4.0133333333333328,5.7799999999999994]
["Eindhoven0313","Eindhoven","03","13",3.6399999999999997,5.8066666666666675]
["Eindhoven0314","Eindhoven","03","14",3.7933333333333339,6.0066666666666659]
["Eindhoven0315","Eindhoven","03","15",4.0066666666666668,7.3733333333333331]
["Eindhoven0316","Eindhoven","03","16",4.0266666666666664,8.2533333333333339]
["Eindhoven0317","Eindhoven","03","17",4.0933333333333328,7.7733333333333325]
["Eindhoven0318","Eindhoven","03","18",4.26,7.0266666666666664]
["Eindhoven0319","Eindhoven","03","19",4.0333333333333341,6.5600000000000005]
["Eindhoven0320","Eindhoven","03","20",3.8933333333333331,6.6999999999999993]
["Eindhoven0321","Eindhoven","03","21",3.753333333333333,6.36]
["Eindhoven0322","Eindhoven","03","22",3.9999999999999991,6.8933333333333335]
["Eindhoven0323","Eindhoven","03","23",3.56,6.8199999999999994]
["Eindhoven0324","Eindhoven","03","24",3.5666666666666673,7.4133333333333322]
["Eindhoven0325","Eindhoven","03","25",3.8666666666666671,7.22]
["Eindhoven0326","Eindhoven","03","26",3.54,7.1866666666666674]
["Eindhoven0327","Eindhoven","03","27",3.4599999999999995,7.7066666666666652]
["Eindhoven0328","Eindhoven","03","28",3.8333333333333335,8.0400000000000009]
["Eindhoven0329","Eindhoven","03","29",3.3066666666666671,8.24]
["Eindhoven0330","Eindhoven","03","30",3.5333333333333323,8.7866666666666653]
["Eindhoven0331","Eindhoven","03","31",4.0266666666666673,9.240000000000002]
["Eindhoven0401","Eindhoven","04","01",4.0999999999999996,9.6999999999999993]
["Eindhoven0402","Eindhoven","04","02",4.1599999999999993,10.846666666666666]
["Eindhoven0403","Eindhoven","04","03",4.0733333333333341,10.286666666666667]
["Eindhoven0404","Eindhoven","04","04",4.2399999999999993,9.0400000000000009]
["Eindhoven0405","Eindhoven","04","05",4.4133333333333349,7.7533333333333339]
["Eindhoven0406","Eindhoven","04","06",4.206666666666667,8.52]
["Eindhoven0407","Eindhoven","04","07",3.7533333333333334,8.1399999999999988]
["Eindhoven0408","Eindhoven","04","08",3.686666666666667,7.16]
["Eindhoven0409","Eindhoven","04","09",3.64,7.9266666666666667]
["Eindhoven0410","Eindhoven","04","10",3.546666666666666,8.5266666666666673]
["Eindhoven0411","Eindhoven","04","11",3.42,8.8933333333333344]
["Eindhoven0412","Eindhoven","04","12",3.8333333333333335,8.8666666666666671]
["Eindhoven0413","Eindhoven","04","13",3.9933333333333332,9.3333333333333357]
["Eindhoven0414","Eindhoven","04","14",3.4733333333333336,10.28]
["Eindhoven0415","Eindhoven","04","15",3.626666666666666,10.766666666666667]
["Eindhoven0416","Eindhoven","04","16",3.3733333333333331,10.459999999999999]
["Eindhoven0417","Eindhoven","04","17",3.6533333333333333,10.726666666666667]
["Eindhoven0418","Eindhoven","04","18",4.58,10.186666666666667]
["Eindhoven0419","Eindhoven","04","19",3.7600000000000002,9.6133333333333333]
["Eindhoven0420","Eindhoven","04","20",3.24,10.246666666666666]
["Eindhoven0421","Eindhoven","04","21",2.9533333333333331,11.173333333333334]
["Eindhoven0422","Eindhoven","04","22",2.6266666666666665,11.213333333333335]
["Eindhoven0423","Eindhoven","04","23",2.6733333333333333,12]
["Eindhoven0424","Eindhoven","04","24",2.7799999999999994,13.646666666666667]
["Eindhoven0425","Eindhoven","04","25",3.38,14.4]
["Eindhoven0426","Eindhoven","04","26",3.5333333333333328,13.166666666666668]
["Eindhoven0427","Eindhoven","04","27",3.98,12.826666666666664]
["Eindhoven0428","Eindhoven","04","28",3.5933333333333333,13.08]
["Eindhoven0429","Eindhoven","04","29",3.9133333333333336,12.719999999999999]
["Eindhoven0430","Eindhoven","04","30",3.7333333333333338,12.933333333333334]
["Eindhoven0501","Eindhoven","05","01",4.1533333333333333,13.373333333333333]
["Eindhoven0502","Eindhoven","05","02",3.8333333333333339,12.466666666666665]
["Eindhoven0503","Eindhoven","05","03",3.5999999999999996,12.366666666666669]
["Eindhoven0504","Eindhoven","05","04",3.9133333333333336,12.22]
["Eindhoven0505","Eindhoven","05","05",3.8533333333333331,12.586666666666668]
["Eindhoven0506","Eindhoven","05","06",3.5733333333333328,13.393333333333334]
["Eindhoven0507","Eindhoven","05","07",3.9466666666666668,13.8]
["Eindhoven0508","Eindhoven","05","08",4.0666666666666664,14.026666666666666]
["Eindhoven0509","Eindhoven","05","09",3.3,14.486666666666668]
["Eindhoven0510","Eindhoven","05","10",3.5733333333333328,15.020000000000003]
["Eindhoven0511","Eindhoven","05","11",4.2733333333333325,13.973333333333333]
["Eindhoven0512","Eindhoven","05","12",3.9133333333333331,12.986666666666666]
["Eindhoven0513","Eindhoven","05","13",3.52,13.733333333333331]
["Eindhoven0514","Eindhoven","05","14",3.62,12.993333333333332]
["Eindhoven0515","Eindhoven","05","15",3.1666666666666665,12.873333333333333]
["Eindhoven0516","Eindhoven","05","16",3.4933333333333336,13.553333333333335]
["Eindhoven0517","Eindhoven","05","17",3.4266666666666667,13.02]
["Eindhoven0518","Eindhoven","05","18",3.7333333333333338,13.393333333333333]
["Eindhoven0519","Eindhoven","05","19",3.8733333333333331,13.753333333333334]
["Eindhoven0520","Eindhoven","05","20",3.5266666666666664,14.186666666666669]
["Eindhoven0521","Eindhoven","05","21",3.5066666666666664,14.793333333333335]
["Eindhoven0522","Eindhoven","05","22",4.0599999999999996,14.726666666666665]
["Eindhoven0523","Eindhoven","05","23",3.42,14.573333333333332]
["Eindhoven0524","Eindhoven","05","24",3.8533333333333339,15.199999999999998]
["Eindhoven0525","Eindhoven","05","25",3.6466666666666665,15.326666666666664]
["Eindhoven0526","Eindhoven","05","26",4.1133333333333333,14.920000000000003]
["Eindhoven0527","Eindhoven","05","27",3.5533333333333332,15.04]
["Eindhoven0528","Eindhoven","05","28",3.9066666666666667,15.58]
["Eindhoven0529","Eindhoven","05","29",3.7933333333333339,14.599999999999998]
["Eindhoven0530","Eindhoven","05","30",2.9866666666666659,14.606666666666667]
["Eindhoven0531","Eindhoven","05","31",3.373333333333334,14.386666666666665]
["Eindhoven0601","Eindhoven","06","01",3.0266666666666664,15.146666666666667]
["Eindhoven0602","Eindhoven","06","02",3.48,16.16]
["Eindhoven0603","Eindhoven","06","03",3.5400000000000005,15.979999999999999]
["Eindhoven0604","Eindhoven","06","04",3.72,15.92]
["Eindhoven0605","Eindhoven","06","05",3.186666666666667,15.493333333333332]
["Eindhoven0606","Eindhoven","06","06",3.0533333333333337,16.119999999999997]
["Eindhoven0607","Eindhoven","06","07",3.1533333333333333,16.506666666666668]
["Eindhoven0608","Eindhoven","06","08",3.166666666666667,17.25333333333333]
["Eindhoven0609","Eindhoven","06","09",3.3533333333333331,17.293333333333333]
["Eindhoven0610","Eindhoven","06","10",2.8066666666666662,16.526666666666664]
["Eindhoven0611","Eindhoven","06","11",3.2866666666666671,15.906666666666668]
["Eindhoven0612","Eindhoven","06","12",3.3266666666666667,15.78]
["Eindhoven0613","Eindhoven","06","13",2.9533333333333331,15.966666666666667]
["Eindhoven0614","Eindhoven","06","14",2.94,16.600000000000001]
["Eindhoven0615","Eindhoven","06","15",3.8,16.286666666666665]
["Eindhoven0616","Eindhoven","06","16",3.5333333333333332,15.9]
["Eindhoven0617","Eindhoven","06","17",3.3533333333333331,17.726666666666667]
["Eindhoven0618","Eindhoven","06","18",3.5466666666666664,18.173333333333332]
["Eindhoven0619","Eindhoven","06","19",3.5266666666666664,17.606666666666666]
["Eindhoven0620","Eindhoven","06","20",3.3533333333333331,17.486666666666668]
["Eindhoven0621","Eindhoven","06","21",3.5733333333333328,16.793333333333333]
["Eindhoven0622","Eindhoven","06","22",3.7866666666666666,16.706666666666671]
["Eindhoven0623","Eindhoven","06","23",4.1266666666666669,16.98]
["Eindhoven0624","Eindhoven","06","24",3.74,17.2]
["Eindhoven0625","Eindhoven","06","25",3.4799999999999995,16.633333333333333]
["Eindhoven0626","Eindhoven","06","26",3.04,17.346666666666668]
["Eindhoven0627","Eindhoven","06","27",3.24,17.98]
["Eindhoven0628","Eindhoven","06","28",3.5666666666666669,18.173333333333332]
["Eindhoven0629","Eindhoven","06","29",3.3666666666666658,17.466666666666665]
["Eindhoven0630","Eindhoven","06","30",3.1733333333333329,18.073333333333334]
["Eindhoven0701","Eindhoven","07","01",3.5799999999999996,17.793333333333337]
["Eindhoven0702","Eindhoven","07","02",3.2333333333333338,18.719999999999995]
["Eindhoven0703","Eindhoven","07","03",3.6133333333333337,18.666666666666668]
["Eindhoven0704","Eindhoven","07","04",3.4399999999999995,18.853333333333335]
["Eindhoven0705","Eindhoven","07","05",3.2933333333333334,18.599999999999998]
["Eindhoven0706","Eindhoven","07","06",3.4,18.2]
["Eindhoven0707","Eindhoven","07","07",3.7933333333333339,17.660000000000004]
["Eindhoven0708","Eindhoven","07","08",3.7266666666666666,17.473333333333336]
["Eindhoven0709","Eindhoven","07","09",3.7933333333333339,17.426666666666666]
["Eindhoven0710","Eindhoven","07","10",3.56,17.600000000000001]
["Eindhoven0711","Eindhoven","07","11",4.1466666666666665,17.346666666666668]
["Eindhoven0712","Eindhoven","07","12",3.5,16.880000000000003]
["Eindhoven0713","Eindhoven","07","13",3.42,17.553333333333335]
["Eindhoven0714","Eindhoven","07","14",3.9733333333333336,17.806666666666668]
["Eindhoven0715","Eindhoven","07","15",3.64,18.853333333333335]
["Eindhoven0716","Eindhoven","07","16",3.4333333333333331,19.473333333333333]
["Eindhoven0717","Eindhoven","07","17",3.7,18.766666666666666]
["Eindhoven0718","Eindhoven","07","18",3.773333333333333,18.980000000000004]
["Eindhoven0719","Eindhoven","07","19",3.4933333333333336,19.379999999999995]
["Eindhoven0720","Eindhoven","07","20",3.1933333333333334,18.360000000000003]
["Eindhoven0721","Eindhoven","07","21",3.1133333333333324,18.313333333333329]
["Eindhoven0722","Eindhoven","07","22",2.6799999999999997,18.82]
["Eindhoven0723","Eindhoven","07","23",2.94,18.486666666666668]
["Eindhoven0724","Eindhoven","07","24",3.36,18.553333333333331]
["Eindhoven0725","Eindhoven","07","25",3.0533333333333328,18.86]
["Eindhoven0726","Eindhoven","07","26",2.7733333333333334,19.379999999999995]
["Eindhoven0727","Eindhoven","07","27",2.5866666666666664,20.059999999999999]
["Eindhoven0728","Eindhoven","07","28",2.686666666666667,19.940000000000001]
["Eindhoven0729","Eindhoven","07","29",2.9999999999999996,19.506666666666664]
["Eindhoven0730","Eindhoven","07","30",3.2600000000000002,18.433333333333334]
["Eindhoven0731","Eindhoven","07","31",2.58,18.420000000000002]
["Eindhoven0801","Eindhoven","08","01",2.6799999999999997,19.320000000000004]
["Eindhoven0802","Eindhoven","08","02",3.0133333333333336,19.266666666666666]
["Eindhoven0803","Eindhoven","08","03",2.6600000000000006,18.273333333333333]
["Eindhoven0804","Eindhoven","08","04",2.9133333333333336,18.773333333333333]
["Eindhoven0805","Eindhoven","08","05",2.9,19.279999999999998]
["Eindhoven0806","Eindhoven","08","06",3.126666666666666,19.38]
["Eindhoven0807","Eindhoven","08","07",3.2,18.673333333333336]
["Eindhoven0808","Eindhoven","08","08",3.3266666666666662,17.993333333333332]
["Eindhoven0809","Eindhoven","08","09",3.24,17.673333333333332]
["Eindhoven0810","Eindhoven","08","10",3.4066666666666663,17.540000000000003]
["Eindhoven0811","Eindhoven","08","11",3.2933333333333326,17.899999999999999]
["Eindhoven0812","Eindhoven","08","12",3.2199999999999998,17.833333333333336]
["Eindhoven0813","Eindhoven","08","13",3.44,17.86]
["Eindhoven0814","Eindhoven","08","14",3.0533333333333332,18.173333333333336]
["Eindhoven0815","Eindhoven","08","15",3.2666666666666662,18.54]
["Eindhoven0816","Eindhoven","08","16",2.7666666666666671,18.213333333333331]
["Eindhoven0817","Eindhoven","08","17",3.4266666666666667,18.226666666666663]
["Eindhoven0818","Eindhoven","08","18",3.3666666666666667,19.166666666666668]
["Eindhoven0819","Eindhoven","08","19",3.7599999999999993,18.813333333333333]
["Eindhoven0820","Eindhoven","08","20",3.04,18.086666666666666]
["Eindhoven0821","Eindhoven","08","21",2.8733333333333335,17.646666666666661]
["Eindhoven0822","Eindhoven","08","22",2.8733333333333335,17.086666666666666]
["Eindhoven0823","Eindhoven","08","23",2.9666666666666672,17.853333333333332]
["Eindhoven0824","Eindhoven","08","24",3.0333333333333323,17.366666666666667]
["Eindhoven0825","Eindhoven","08","25",2.9266666666666663,17.253333333333334]
["Eindhoven0826","Eindhoven","08","26",3.7399999999999993,17.440000000000001]
["Eindhoven0827","Eindhoven","08","27",3.2666666666666662,16.613333333333333]
["Eindhoven0828","Eindhoven","08","28",3.273333333333333,16.15333333333334]
["Eindhoven0829","Eindhoven","08","29",3.2733333333333334,15.586666666666666]
["Eindhoven0830","Eindhoven","08","30",3.42,15.520000000000003]
["Eindhoven0831","Eindhoven","08","31",3.3,16.09333333333333]
["Eindhoven0901","Eindhoven","09","01",2.9266666666666667,15.426666666666668]
["Eindhoven0902","Eindhoven","09","02",3.4,16.353333333333335]
["Eindhoven0903","Eindhoven","09","03",3.5533333333333337,16.720000000000002]
["Eindhoven0904","Eindhoven","09","04",3.1133333333333337,16.633333333333333]
["Eindhoven0905","Eindhoven","09","05",3.0933333333333333,16.880000000000003]
["Eindhoven0906","Eindhoven","09","06",3.5066666666666668,16.993333333333332]
["Eindhoven0907","Eindhoven","09","07",3.58,16.253333333333334]
["Eindhoven0908","Eindhoven","09","08",3.2066666666666661,16.32]
["Eindhoven0909","Eindhoven","09","09",2.9866666666666664,16.233333333333331]
["Eindhoven0910","Eindhoven","09","10",3.3266666666666671,16.366666666666667]
["Eindhoven0911","Eindhoven","09","11",3.3200000000000007,16.386666666666667]
["Eindhoven0912","Eindhoven","09","12",3.4599999999999995,15.613333333333333]
["Eindhoven0913","Eindhoven","09","13",3.3666666666666667,14.946666666666667]
["Eindhoven0914","Eindhoven","09","14",3.9200000000000004,14.886666666666667]
["Eindhoven0915","Eindhoven","09","15",3.4,14.926666666666669]
["Eindhoven0916","Eindhoven","09","16",3.14,14.26]
["Eindhoven0917","Eindhoven","09","17",3.0933333333333337,13.726666666666667]
["Eindhoven0918","Eindhoven","09","18",2.9000000000000004,13.813333333333333]
["Eindhoven0919","Eindhoven","09","19",3.2066666666666666,13.78]
["Eindhoven0920","Eindhoven","09","20",3.246666666666667,14.426666666666668]
["Eindhoven0921","Eindhoven","09","21",2.7866666666666671,14.333333333333334]
["Eindhoven0922","Eindhoven","09","22",3.22,14.446666666666669]
["Eindhoven0923","Eindhoven","09","23",2.9733333333333336,13.933333333333334]
["Eindhoven0924","Eindhoven","09","24",3.0333333333333332,13.753333333333336]
["Eindhoven0925","Eindhoven","09","25",3.0999999999999996,13.226666666666667]
["Eindhoven0926","Eindhoven","09","26",2.8933333333333331,13.433333333333334]
["Eindhoven0927","Eindhoven","09","27",2.7199999999999993,13.359999999999998]
["Eindhoven0928","Eindhoven","09","28",2.9533333333333331,14.046666666666669]
["Eindhoven0929","Eindhoven","09","29",3.2066666666666661,13.980000000000002]
["Eindhoven0930","Eindhoven","09","30",3.08,13.413333333333332]
["Eindhoven1001","Eindhoven","10","01",3.4466666666666663,13.72]
["Eindhoven1002","Eindhoven","10","02",3.6200000000000006,13.606666666666667]
["Eindhoven1003","Eindhoven","10","03",3.56,13.913333333333334]
["Eindhoven1004","Eindhoven","10","04",3.7666666666666671,13.386666666666667]
["Eindhoven1005","Eindhoven","10","05",3.7866666666666671,12.979999999999997]
["Eindhoven1006","Eindhoven","10","06",3.9799999999999995,12.766666666666669]
["Eindhoven1007","Eindhoven","10","07",3.3333333333333339,11.853333333333333]
["Eindhoven1008","Eindhoven","10","08",3.1866666666666665,11.513333333333334]
["Eindhoven1009","Eindhoven","10","09",3.4066666666666667,11.740000000000002]
["Eindhoven1010","Eindhoven","10","10",4.0333333333333332,12.206666666666669]
["Eindhoven1011","Eindhoven","10","11",3.7666666666666666,11.426666666666666]
["Eindhoven1012","Eindhoven","10","12",3.3066666666666662,11.460000000000003]
["Eindhoven1013","Eindhoven","10","13",3.18,11.486666666666666]
["Eindhoven1014","Eindhoven","10","14",3.2533333333333334,10.873333333333333]
["Eindhoven1015","Eindhoven","10","15",3.4866666666666664,10.979999999999999]
["Eindhoven1016","Eindhoven","10","16",4.0133333333333328,10.613333333333333]
["Eindhoven1017","Eindhoven","10","17",3.7133333333333334,10.146666666666667]
["Eindhoven1018","Eindhoven","10","18",3.5666666666666669,10.586666666666666]
["Eindhoven1019","Eindhoven","10","19",3.4133333333333327,10.873333333333333]
["Eindhoven1020","Eindhoven","10","20",3.5999999999999996,10.933333333333334]
["Eindhoven1021","Eindhoven","10","21",4.0666666666666664,11.219999999999999]
["Eindhoven1022","Eindhoven","10","22",3.7333333333333334,10.826666666666664]
["Eindhoven1023","Eindhoven","10","23",4.3599999999999994,10.653333333333334]
["Eindhoven1024","Eindhoven","10","24",4.3066666666666666,10.226666666666667]
["Eindhoven1025","Eindhoven","10","25",4.6466666666666656,11.033333333333335]
["Eindhoven1026","Eindhoven","10","26",4.4666666666666668,11.026666666666667]
["Eindhoven1027","Eindhoven","10","27",4.1933333333333325,10.080000000000002]
["Eindhoven1028","Eindhoven","10","28",3.8333333333333335,9.9066666666666681]
["Eindhoven1029","Eindhoven","10","29",3.5666666666666669,10.093333333333334]
["Eindhoven1030","Eindhoven","10","30",3.4999999999999996,10.18]
["Eindhoven1031","Eindhoven","10","31",3.8466666666666671,10.073333333333334]
["Eindhoven1101","Eindhoven","11","01",4.046666666666666,9.759999999999998]
["Eindhoven1102","Eindhoven","11","02",4.1066666666666665,10.120000000000001]
["Eindhoven1103","Eindhoven","11","03",4.5533333333333328,10.46]
["Eindhoven1104","Eindhoven","11","04",3.7666666666666662,9.413333333333334]
["Eindhoven1105","Eindhoven","11","05",3.7800000000000002,8.5266666666666655]
["Eindhoven1106","Eindhoven","11","06",3.9933333333333332,8.9466666666666654]
["Eindhoven1107","Eindhoven","11","07",4.0199999999999996,8.3066666666666666]
["Eindhoven1108","Eindhoven","11","08",4.5200000000000005,8.1]
["Eindhoven1109","Eindhoven","11","09",3.86,7.34]
["Eindhoven1110","Eindhoven","11","10",3.8200000000000003,7.12]
["Eindhoven1111","Eindhoven","11","11",4.7133333333333329,7.48]
["Eindhoven1112","Eindhoven","11","12",4.22,7.6599999999999993]
["Eindhoven1113","Eindhoven","11","13",3.5733333333333333,7.9733333333333336]
["Eindhoven1114","Eindhoven","11","14",3.8133333333333339,7.4133333333333331]
["Eindhoven1115","Eindhoven","11","15",3.0999999999999996,6.3199999999999994]
["Eindhoven1116","Eindhoven","11","16",2.8533333333333335,6.2866666666666653]
["Eindhoven1117","Eindhoven","11","17",3.36,6.6066666666666674]
["Eindhoven1118","Eindhoven","11","18",3.526666666666666,6.7466666666666653]
["Eindhoven1119","Eindhoven","11","19",3.26,6.4800000000000013]
["Eindhoven1120","Eindhoven","11","20",3.7733333333333334,6.4800000000000013]
["Eindhoven1121","Eindhoven","11","21",4.2066666666666661,6.38]
["Eindhoven1122","Eindhoven","11","22",4.4599999999999991,6.8266666666666671]
["Eindhoven1123","Eindhoven","11","23",3.7266666666666661,6.7733333333333343]
["Eindhoven1124","Eindhoven","11","24",3.3866666666666663,5.9933333333333332]
["Eindhoven1125","Eindhoven","11","25",4.7333333333333334,6.2200000000000006]
["Eindhoven1126","Eindhoven","11","26",4.0266666666666664,5.62]
["Eindhoven1127","Eindhoven","11","27",3.4666666666666663,5.4799999999999995]
["Eindhoven1128","Eindhoven","11","28",3.3866666666666663,5.6866666666666674]
["Eindhoven1129","Eindhoven","11","29",3.78,5.5266666666666673]
["Eindhoven1130","Eindhoven","11","30",3.246666666666667,5.0933333333333328]
["Eindhoven1201","Eindhoven","12","01",4.1866666666666665,5.666666666666667]
["Eindhoven1202","Eindhoven","12","02",3.76,4.84]
["Eindhoven1203","Eindhoven","12","03",3.8599999999999994,4.120000000000001]
["Eindhoven1204","Eindhoven","12","04",4.6133333333333333,4.7600000000000007]
["Eindhoven1205","Eindhoven","12","05",4.8400000000000007,6.0866666666666678]
["Eindhoven1206","Eindhoven","12","06",4.5333333333333323,5.3266666666666671]
["Eindhoven1207","Eindhoven","12","07",4.5666666666666664,4.1733333333333338]
["Eindhoven1208","Eindhoven","12","08",4.4666666666666659,3.7133333333333338]
["Eindhoven1209","Eindhoven","12","09",4.1399999999999997,3.2066666666666674]
["Eindhoven1210","Eindhoven","12","10",3.6533333333333333,2.5466666666666669]
["Eindhoven1211","Eindhoven","12","11",4.24,3.6399999999999997]
["Eindhoven1212","Eindhoven","12","12",4.1866666666666665,3.7466666666666675]
["Eindhoven1213","Eindhoven","12","13",4.58,3.2066666666666661]
["Eindhoven1214","Eindhoven","12","14",4.3533333333333335,2.9733333333333336]
["Eindhoven1215","Eindhoven","12","15",4.5466666666666669,3.6333333333333329]
["Eindhoven1216","Eindhoven","12","16",4.3866666666666667,3.5066666666666668]
["Eindhoven1217","Eindhoven","12","17",3.6599999999999997,2.4333333333333331]
["Eindhoven1218","Eindhoven","12","18",3.3533333333333335,2.3133333333333335]
["Eindhoven1219","Eindhoven","12","19",3.4666666666666668,2.0266666666666668]
["Eindhoven1220","Eindhoven","12","20",3.9866666666666668,1.6933333333333329]
["Eindhoven1221","Eindhoven","12","21",4.0666666666666664,3.0266666666666664]
["Eindhoven1222","Eindhoven","12","22",4.4733333333333336,4.0733333333333341]
["Eindhoven1223","Eindhoven","12","23",4.5066666666666659,4.2333333333333334]
["Eindhoven1224","Eindhoven","12","24",5.0266666666666673,4.7933333333333339]
["Eindhoven1225","Eindhoven","12","25",4.5999999999999988,4.3600000000000003]
["Eindhoven1226","Eindhoven","12","26",4.1466666666666665,3.3199999999999994]
["Eindhoven1227","Eindhoven","12","27",4.7000000000000011,2.9266666666666667]
["Eindhoven1228","Eindhoven","12","28",4.7466666666666661,3.1533333333333333]
["Eindhoven1229","Eindhoven","12","29",4.2266666666666666,3.1466666666666665]
["Eindhoven1230","Eindhoven","12","30",4.5399999999999983,3.0266666666666664]
["Eindhoven1231","Eindhoven","12","31",4.3266666666666662,3.4066666666666672]
["Lauwersoog0101","Lauwersoog","01","01",6.4266666666666659,3.4533333333333331]
["Lauwersoog0102","Lauwersoog","01","02",6.28,3.4466666666666672]
["Lauwersoog0103","Lauwersoog","01","03",7.0933333333333337,3.0133333333333336]
["Lauwersoog0104","Lauwersoog","01","04",7.660000000000001,3.2199999999999998]
["Lauwersoog0105","Lauwersoog","01","05",7.2066666666666661,3.2666666666666666]
["Lauwersoog0106","Lauwersoog","01","06",6.6266666666666669,3.7]
["Lauwersoog0107","Lauwersoog","01","07",6.5133333333333319,3.9533333333333336]
["Lauwersoog0108","Lauwersoog","01","08",6.8266666666666662,3.8799999999999994]
["Lauwersoog0109","Lauwersoog","01","09",6.7333333333333334,3.4933333333333336]
["Lauwersoog0110","Lauwersoog","01","10",7.0533333333333328,3.1466666666666665]
["Lauwersoog0111","Lauwersoog","01","11",7.2333333333333334,3.8666666666666667]
["Lauwersoog0112","Lauwersoog","01","12",6.8199999999999994,3.4533333333333336]
["Lauwersoog0113","Lauwersoog","01","13",7.5066666666666659,3.3866666666666672]
["Lauwersoog0114","Lauwersoog","01","14",5.98,3.3333333333333339]
["Lauwersoog0115","Lauwersoog","01","15",5.8333333333333339,2.753333333333333]
["Lauwersoog0116","Lauwersoog","01","16",6.1999999999999993,2.9933333333333332]
["Lauwersoog0117","Lauwersoog","01","17",6.799999999999998,3.5666666666666673]
["Lauwersoog0118","Lauwersoog","01","18",6.9533333333333331,3.6600000000000006]
["Lauwersoog0119","Lauwersoog","01","19",7.5866666666666651,4.0200000000000005]
["Lauwersoog0120","Lauwersoog","01","20",8.2066666666666652,4.16]
["Lauwersoog0121","Lauwersoog","01","21",7.5266666666666673,3.4666666666666668]
["Lauwersoog0122","Lauwersoog","01","22",7.4333333333333336,2.5533333333333337]
["Lauwersoog0123","Lauwersoog","01","23",6.7133333333333329,2.3199999999999994]
["Lauwersoog0124","Lauwersoog","01","24",6.3199999999999985,2.2800000000000002]
["Lauwersoog0125","Lauwersoog","01","25",6.7266666666666675,1.7866666666666662]
["Lauwersoog0126","Lauwersoog","01","26",7.1,2.1800000000000006]
["Lauwersoog0127","Lauwersoog","01","27",6.4733333333333336,2.8333333333333335]
["Lauwersoog0128","Lauwersoog","01","28",7.1399999999999988,2.9266666666666672]
["Lauwersoog0129","Lauwersoog","01","29",6.9066666666666654,2.78]
["Lauwersoog0130","Lauwersoog","01","30",6.9066666666666663,2.773333333333333]
["Lauwersoog0131","Lauwersoog","01","31",7.8066666666666675,2.7066666666666666]
["Lauwersoog0201","Lauwersoog","02","01",7.6466666666666656,2.9333333333333327]
["Lauwersoog0202","Lauwersoog","02","02",7.8733333333333331,3.5800000000000005]
["Lauwersoog0203","Lauwersoog","02","03",6.8066666666666666,3.399999999999999]
["Lauwersoog0204","Lauwersoog","02","04",7,3.5333333333333328]
["Lauwersoog0205","Lauwersoog","02","05",7.1666666666666661,4.046666666666666]
["Lauwersoog0206","Lauwersoog","02","06",6.6533333333333333,3.9733333333333332]
["Lauwersoog0207","Lauwersoog","02","07",7.16,3.5666666666666655]
["Lauwersoog0208","Lauwersoog","02","08",7.6933333333333325,3.2533333333333334]
["Lauwersoog0209","Lauwersoog","02","09",7.3533333333333326,3.1066666666666669]
["Lauwersoog0210","Lauwersoog","02","10",7.2333333333333334,2.753333333333333]
["Lauwersoog0211","Lauwersoog","02","11",6.0933333333333337,3.0000000000000004]
["Lauwersoog0212","Lauwersoog","02","12",6.7933333333333339,2.9333333333333331]
["Lauwersoog0213","Lauwersoog","02","13",6.0666666666666664,3.2133333333333325]
["Lauwersoog0214","Lauwersoog","02","14",5.666666666666667,2.7733333333333334]
["Lauwersoog0215","Lauwersoog","02","15",5.8733333333333331,2.9733333333333336]
["Lauwersoog0216","Lauwersoog","02","16",5.5600000000000005,3]
["Lauwersoog0217","Lauwersoog","02","17",4.8533333333333326,2.4466666666666668]
["Lauwersoog0218","Lauwersoog","02","18",5.4133333333333322,3.1799999999999997]
["Lauwersoog0219","Lauwersoog","02","19",6.8733333333333331,2.9066666666666667]
["Lauwersoog0220","Lauwersoog","02","20",7.1533333333333333,2.74]
["Lauwersoog0221","Lauwersoog","02","21",6.9399999999999986,2.8133333333333335]
["Lauwersoog0222","Lauwersoog","02","22",8.4400000000000013,3.3333333333333339]
["Lauwersoog0223","Lauwersoog","02","23",7.8,3.38]
["Lauwersoog0224","Lauwersoog","02","24",6.7399999999999993,3.8733333333333331]
["Lauwersoog0225","Lauwersoog","02","25",6.373333333333334,4.04]
["Lauwersoog0226","Lauwersoog","02","26",6.8133333333333326,4.3666666666666663]
["Lauwersoog0227","Lauwersoog","02","27",6.6333333333333337,3.6133333333333337]
["Lauwersoog0228","Lauwersoog","02","28",5.8466666666666676,4.24]
["Lauwersoog0229","Lauwersoog","02","29",6.7750000000000004,5.1750000000000007]
["Lauwersoog0301","Lauwersoog","03","01",7.1933333333333325,4.2]
["Lauwersoog0302","Lauwersoog","03","02",6.953333333333334,3.6199999999999997]
["Lauwersoog0303","Lauwersoog","03","03",6.2733333333333317,3.3733333333333344]
["Lauwersoog0304","Lauwersoog","03","04",6.56,3.5666666666666669]
["Lauwersoog0305","Lauwersoog","03","05",5.9666666666666668,4.293333333333333]
["Lauwersoog0306","Lauwersoog","03","06",7.0466666666666677,4.6266666666666669]
["Lauwersoog0307","Lauwersoog","03","07",6.56,4.9399999999999995]
["Lauwersoog0308","Lauwersoog","03","08",7.1199999999999992,5.4866666666666664]
["Lauwersoog0309","Lauwersoog","03","09",7.7533333333333339,5.5133333333333345]
["Lauwersoog0310","Lauwersoog","03","10",7.7466666666666661,5.36]
["Lauwersoog0311","Lauwersoog","03","11",8.0666666666666664,5.4399999999999995]
["Lauwersoog0312","Lauwersoog","03","12",6.3599999999999994,5.4666666666666668]
["Lauwersoog0313","Lauwersoog","03","13",5.8133333333333326,5.3066666666666666]
["Lauwersoog0314","Lauwersoog","03","14",6.6066666666666665,5.2866666666666662]
["Lauwersoog0315","Lauwersoog","03","15",7.4933333333333332,5.56]
["Lauwersoog0316","Lauwersoog","03","16",7.1733333333333338,6.3866666666666667]
["Lauwersoog0317","Lauwersoog","03","17",7.7799999999999985,6.419999999999999]
["Lauwersoog0318","Lauwersoog","03","18",7.44,6.1533333333333342]
["Lauwersoog0319","Lauwersoog","03","19",7.3199999999999994,5.4266666666666676]
["Lauwersoog0320","Lauwersoog","03","20",6.1266666666666669,5.953333333333334]
["Lauwersoog0321","Lauwersoog","03","21",6.1466666666666647,5.5999999999999988]
["Lauwersoog0322","Lauwersoog","03","22",6.8533333333333326,5.5333333333333323]
["Lauwersoog0323","Lauwersoog","03","23",6.546666666666666,5.5400000000000009]
["Lauwersoog0324","Lauwersoog","03","24",6.42,6.1333333333333337]
["Lauwersoog0325","Lauwersoog","03","25",6.246666666666667,6.3133333333333335]
["Lauwersoog0326","Lauwersoog","03","26",5.5533333333333319,6.1933333333333334]
["Lauwersoog0327","Lauwersoog","03","27",6.3133333333333335,6.3533333333333335]
["Lauwersoog0328","Lauwersoog","03","28",6.6933333333333325,6.8133333333333344]
["Lauwersoog0329","Lauwersoog","03","29",5.78,7.06]
["Lauwersoog0330","Lauwersoog","03","30",6.3466666666666658,7.7]
["Lauwersoog0331","Lauwersoog","03","31",6.3999999999999995,7.753333333333333]
["Lauwersoog0401","Lauwersoog","04","01",6.3466666666666658,8.18]
["Lauwersoog0402","Lauwersoog","04","02",6.6266666666666678,9.2200000000000006]
["Lauwersoog0403","Lauwersoog","04","03",6.9,8.7133333333333347]
["Lauwersoog0404","Lauwersoog","04","04",7.2933333333333339,7.8000000000000007]
["Lauwersoog0405","Lauwersoog","04","05",7.8533333333333335,7.2266666666666657]
["Lauwersoog0406","Lauwersoog","04","06",6.4866666666666655,7.833333333333333]
["Lauwersoog0407","Lauwersoog","04","07",5.9,7.8066666666666675]
["Lauwersoog0408","Lauwersoog","04","08",6.5933333333333337,7.04]
["Lauwersoog0409","Lauwersoog","04","09",6.4533333333333323,7.4066666666666672]
["Lauwersoog0410","Lauwersoog","04","10",5.9,8.0599999999999987]
["Lauwersoog0411","Lauwersoog","04","11",5.3733333333333331,8.2999999999999989]
["Lauwersoog0412","Lauwersoog","04","12",6.2999999999999989,8.24]
["Lauwersoog0413","Lauwersoog","04","13",5.9,8.3933333333333344]
["Lauwersoog0414","Lauwersoog","04","14",5.9733333333333327,9.1133333333333333]
["Lauwersoog0415","Lauwersoog","04","15",5.96,10.319999999999999]
["Lauwersoog0416","Lauwersoog","04","16",5.9933333333333341,9.793333333333333]
["Lauwersoog0417","Lauwersoog","04","17",6.5333333333333341,9.6133333333333333]
["Lauwersoog0418","Lauwersoog","04","18",7.5333333333333323,9.3199999999999985]
["Lauwersoog0419","Lauwersoog","04","19",6.9133333333333322,9.2199999999999989]
["Lauwersoog0420","Lauwersoog","04","20",6.0466666666666669,9.6133333333333333]
["Lauwersoog0421","Lauwersoog","04","21",5.5066666666666668,10.186666666666666]
["Lauwersoog0422","Lauwersoog","04","22",5.2399999999999993,10.373333333333333]
["Lauwersoog0423","Lauwersoog","04","23",4.8333333333333339,10.553333333333335]
["Lauwersoog0424","Lauwersoog","04","24",4.8466666666666667,12.066666666666666]
["Lauwersoog0425","Lauwersoog","04","25",5.206666666666667,13.066666666666665]
["Lauwersoog0426","Lauwersoog","04","26",5.6400000000000006,11.873333333333335]
["Lauwersoog0427","Lauwersoog","04","27",6.24,11.46]
["Lauwersoog0428","Lauwersoog","04","28",6.2600000000000007,11.933333333333332]
["Lauwersoog0429","Lauwersoog","04","29",6.3066666666666666,11.606666666666666]
["Lauwersoog0430","Lauwersoog","04","30",6.1866666666666656,11.373333333333331]
["Lauwersoog0501","Lauwersoog","05","01",6.4866666666666664,10.933333333333334]
["Lauwersoog0502","Lauwersoog","05","02",6.7533333333333321,10.740000000000002]
["Lauwersoog0503","Lauwersoog","05","03",6.6733333333333329,11.020000000000001]
["Lauwersoog0504","Lauwersoog","05","04",6.9733333333333327,11.140000000000002]
["Lauwersoog0505","Lauwersoog","05","05",6.6466666666666665,11.486666666666668]
["Lauwersoog0506","Lauwersoog","05","06",6.9466666666666672,12.24]
["Lauwersoog0507","Lauwersoog","05","07",7.02,12.673333333333334]
["Lauwersoog0508","Lauwersoog","05","08",6.7199999999999989,12.72]
["Lauwersoog0509","Lauwersoog","05","09",5.793333333333333,13.020000000000001]
["Lauwersoog0510","Lauwersoog","05","10",6.3266666666666662,13.646666666666667]
["Lauwersoog0511","Lauwersoog","05","11",6.76,12.3]
["Lauwersoog0512","Lauwersoog","05","12",7.4599999999999982,12.193333333333335]
["Lauwersoog0513","Lauwersoog","05","13",6.5,12.42]
["Lauwersoog0514","Lauwersoog","05","14",7.0533333333333319,11.94]
["Lauwersoog0515","Lauwersoog","05","15",6.1333333333333337,12.306666666666667]
["Lauwersoog0516","Lauwersoog","05","16",6.2800000000000011,12.333333333333332]
["Lauwersoog0517","Lauwersoog","05","17",5.4333333333333336,12.046666666666669]
["Lauwersoog0518","Lauwersoog","05","18",6.333333333333333,12.706666666666669]
["Lauwersoog0519","Lauwersoog","05","19",5.6666666666666661,12.773333333333333]
["Lauwersoog0520","Lauwersoog","05","20",5.1133333333333324,13.606666666666667]
["Lauwersoog0521","Lauwersoog","05","21",5.9866666666666664,13.740000000000002]
["Lauwersoog0522","Lauwersoog","05","22",6.6800000000000006,13.673333333333337]
["Lauwersoog0523","Lauwersoog","05","23",6.1066666666666656,13.78]
["Lauwersoog0524","Lauwersoog","05","24",6.3466666666666649,13.433333333333335]
["Lauwersoog0525","Lauwersoog","05","25",6.5199999999999987,13.326666666666664]
["Lauwersoog0526","Lauwersoog","05","26",7.0666666666666664,13.753333333333332]
["Lauwersoog0527","Lauwersoog","05","27",6.6133333333333333,13.933333333333332]
["Lauwersoog0528","Lauwersoog","05","28",6.5733333333333333,13.793333333333335]
["Lauwersoog0529","Lauwersoog","05","29",6.9666666666666659,13.666666666666664]
["Lauwersoog0530","Lauwersoog","05","30",5.4066666666666654,14.266666666666667]
["Lauwersoog0531","Lauwersoog","05","31",6.7533333333333339,13.466666666666665]
["Lauwersoog0601","Lauwersoog","06","01",6.2866666666666671,13.993333333333334]
["Lauwersoog0602","Lauwersoog","06","02",6.44,14.706666666666669]
["Lauwersoog0603","Lauwersoog","06","03",6.9,14.62]
["Lauwersoog0604","Lauwersoog","06","04",6.84,14.680000000000001]
["Lauwersoog0605","Lauwersoog","06","05",5.9000000000000012,14.346666666666668]
["Lauwersoog0606","Lauwersoog","06","06",5.7733333333333343,14.966666666666667]
["Lauwersoog0607","Lauwersoog","06","07",5.62,15.199999999999998]
["Lauwersoog0608","Lauwersoog","06","08",4.8533333333333335,15.92]
["Lauwersoog0609","Lauwersoog","06","09",5.2133333333333347,16.12]
["Lauwersoog0610","Lauwersoog","06","10",5.0733333333333333,15.740000000000004]
["Lauwersoog0611","Lauwersoog","06","11",6.3599999999999994,15.299999999999999]
["Lauwersoog0612","Lauwersoog","06","12",6.24,15.140000000000002]
["Lauwersoog0613","Lauwersoog","06","13",6.2133333333333347,15.053333333333335]
["Lauwersoog0614","Lauwersoog","06","14",5.5,14.953333333333335]
["Lauwersoog0615","Lauwersoog","06","15",6.206666666666667,15.013333333333332]
["Lauwersoog0616","Lauwersoog","06","16",6.06,14.753333333333332]
["Lauwersoog0617","Lauwersoog","06","17",5.8733333333333331,15.860000000000003]
["Lauwersoog0618","Lauwersoog","06","18",5.8866666666666667,16.160000000000004]
["Lauwersoog0619","Lauwersoog","06","19",6.8,16.446666666666665]
["Lauwersoog0620","Lauwersoog","06","20",6.7666666666666657,16.46]
["Lauwersoog0621","Lauwersoog","06","21",5.7666666666666666,15.893333333333336]
["Lauwersoog0622","Lauwersoog","06","22",6.126666666666666,15.84]
["Lauwersoog0623","Lauwersoog","06","23",6.0933333333333337,15.973333333333334]
["Lauwersoog0624","Lauwersoog","06","24",6.6266666666666669,15.42]
["Lauwersoog0625","Lauwersoog","06","25",7.1133333333333333,15.513333333333332]
["Lauwersoog0626","Lauwersoog","06","26",6.74,15.800000000000002]
["Lauwersoog0627","Lauwersoog","06","27",6.5133333333333328,16.373333333333338]
["Lauwersoog0628","Lauwersoog","06","28",6.26,16.880000000000003]
["Lauwersoog0629","Lauwersoog","06","29",6.0999999999999988,16.286666666666669]
["Lauwersoog0630","Lauwersoog","06","30",5.4533333333333331,16.506666666666668]
["Lauwersoog0701","Lauwersoog","07","01",5.793333333333333,16.606666666666669]
["Lauwersoog0702","Lauwersoog","07","02",5.4466666666666681,17.913333333333334]
["Lauwersoog0703","Lauwersoog","07","03",5.44,17.793333333333337]
["Lauwersoog0704","Lauwersoog","07","04",5.6133333333333342,18.166666666666664]
["Lauwersoog0705","Lauwersoog","07","05",4.9466666666666672,18.226666666666667]
["Lauwersoog0706","Lauwersoog","07","06",5.546666666666666,17.646666666666665]
["Lauwersoog0707","Lauwersoog","07","07",5.7,17.280000000000005]
["Lauwersoog0708","Lauwersoog","07","08",5.8333333333333313,17.266666666666666]
["Lauwersoog0709","Lauwersoog","07","09",5.98,17.413333333333334]
["Lauwersoog0710","Lauwersoog","07","10",5.9000000000000012,17.473333333333336]
["Lauwersoog0711","Lauwersoog","07","11",6.8066666666666684,16.886666666666667]
["Lauwersoog0712","Lauwersoog","07","12",6.4666666666666668,16.513333333333335]
["Lauwersoog0713","Lauwersoog","07","13",5.92,16.713333333333331]
["Lauwersoog0714","Lauwersoog","07","14",5.6266666666666669,17.626666666666665]
["Lauwersoog0715","Lauwersoog","07","15",6.4733333333333327,17.720000000000002]
["Lauwersoog0716","Lauwersoog","07","16",5.6333333333333337,17.86]
["Lauwersoog0717","Lauwersoog","07","17",5.7133333333333347,17.766666666666666]
["Lauwersoog0718","Lauwersoog","07","18",6.1733333333333329,17.533333333333335]
["Lauwersoog0719","Lauwersoog","07","19",6.206666666666667,18.420000000000002]
["Lauwersoog0720","Lauwersoog","07","20",6.66,18.086666666666662]
["Lauwersoog0721","Lauwersoog","07","21",6.6800000000000015,17.893333333333334]
["Lauwersoog0722","Lauwersoog","07","22",6.419999999999999,18.059999999999999]
["Lauwersoog0723","Lauwersoog","07","23",5.7399999999999993,18.32]
["Lauwersoog0724","Lauwersoog","07","24",6.1866666666666665,18.033333333333335]
["Lauwersoog0725","Lauwersoog","07","25",5.1066666666666674,18.153333333333329]
["Lauwersoog0726","Lauwersoog","07","26",5.246666666666667,18.433333333333334]
["Lauwersoog0727","Lauwersoog","07","27",4.1133333333333342,19.166666666666668]
["Lauwersoog0728","Lauwersoog","07","28",4.8533333333333344,19.206666666666667]
["Lauwersoog0729","Lauwersoog","07","29",5.1466666666666656,19.27333333333333]
["Lauwersoog0730","Lauwersoog","07","30",6.06,18.173333333333336]
["Lauwersoog0731","Lauwersoog","07","31",5.2,18.380000000000003]
["Lauwersoog0801","Lauwersoog","08","01",4.6266666666666669,18.913333333333334]
["Lauwersoog0802","Lauwersoog","08","02",4.4800000000000004,19.146666666666661]
["Lauwersoog0803","Lauwersoog","08","03",4.626666666666666,18.279999999999998]
["Lauwersoog0804","Lauwersoog","08","04",5.1133333333333324,18.366666666666667]
["Lauwersoog0805","Lauwersoog","08","05",5.1533333333333333,19.293333333333333]
["Lauwersoog0806","Lauwersoog","08","06",5.4333333333333327,19.286666666666665]
["Lauwersoog0807","Lauwersoog","08","07",5.6800000000000006,18.84]
["Lauwersoog0808","Lauwersoog","08","08",6.7800000000000011,18.293333333333337]
["Lauwersoog0809","Lauwersoog","08","09",6.42,18.193333333333332]
["Lauwersoog0810","Lauwersoog","08","10",6.0266666666666664,17.853333333333332]
["Lauwersoog0811","Lauwersoog","08","11",5.546666666666666,17.646666666666661]
["Lauwersoog0812","Lauwersoog","08","12",5.3,17.573333333333334]
["Lauwersoog0813","Lauwersoog","08","13",5.8333333333333321,17.666666666666668]
["Lauwersoog0814","Lauwersoog","08","14",5.4866666666666664,18.233333333333338]
["Lauwersoog0815","Lauwersoog","08","15",6.12,18.633333333333329]
["Lauwersoog0816","Lauwersoog","08","16",4.8666666666666663,17.993333333333336]
["Lauwersoog0817","Lauwersoog","08","17",4.96,18.106666666666666]
["Lauwersoog0818","Lauwersoog","08","18",5.293333333333333,18.760000000000002]
["Lauwersoog0819","Lauwersoog","08","19",5.6999999999999993,18.559999999999999]
["Lauwersoog0820","Lauwersoog","08","20",5.1466666666666665,18.12]
["Lauwersoog0821","Lauwersoog","08","21",4.76,17.673333333333332]
["Lauwersoog0822","Lauwersoog","08","22",5.1799999999999988,17.553333333333331]
["Lauwersoog0823","Lauwersoog","08","23",4.7866666666666662,17.579999999999998]
["Lauwersoog0824","Lauwersoog","08","24",4.8333333333333321,17.566666666666666]
["Lauwersoog0825","Lauwersoog","08","25",5.0533333333333328,17.66]
["Lauwersoog0826","Lauwersoog","08","26",6.4266666666666676,17.440000000000001]
["Lauwersoog0827","Lauwersoog","08","27",6.253333333333333,16.966666666666665]
["Lauwersoog0828","Lauwersoog","08","28",5.7866666666666653,16.446666666666665]
["Lauwersoog0829","Lauwersoog","08","29",5.6066666666666656,16.206666666666667]
["Lauwersoog0830","Lauwersoog","08","30",6.0733333333333341,16.493333333333329]
["Lauwersoog0831","Lauwersoog","08","31",6.746666666666667,16.733333333333334]
["Lauwersoog0901","Lauwersoog","09","01",5.8133333333333335,16.313333333333333]
["Lauwersoog0902","Lauwersoog","09","02",5.4933333333333341,16.46]
["Lauwersoog0903","Lauwersoog","09","03",5.9866666666666664,16.606666666666669]
["Lauwersoog0904","Lauwersoog","09","04",6.120000000000001,16.513333333333332]
["Lauwersoog0905","Lauwersoog","09","05",5.2133333333333329,16.766666666666666]
["Lauwersoog0906","Lauwersoog","09","06",6.0333333333333332,16.82]
["Lauwersoog0907","Lauwersoog","09","07",6.4666666666666677,16.40666666666667]
["Lauwersoog0908","Lauwersoog","09","08",6.6466666666666665,16.393333333333334]
["Lauwersoog0909","Lauwersoog","09","09",6.0666666666666664,16.433333333333334]
["Lauwersoog0910","Lauwersoog","09","10",6.6000000000000005,16.48]
["Lauwersoog0911","Lauwersoog","09","11",6.8533333333333344,16.880000000000003]
["Lauwersoog0912","Lauwersoog","09","12",6.3733333333333331,16.459999999999997]
["Lauwersoog0913","Lauwersoog","09","13",5.8333333333333321,15.899999999999997]
["Lauwersoog0914","Lauwersoog","09","14",7.3199999999999994,15.759999999999998]
["Lauwersoog0915","Lauwersoog","09","15",6.746666666666667,15.273333333333333]
["Lauwersoog0916","Lauwersoog","09","16",6.1933333333333334,15]
["Lauwersoog0917","Lauwersoog","09","17",5.4533333333333331,14.926666666666668]
["Lauwersoog0918","Lauwersoog","09","18",5.5866666666666651,14.366666666666665]
["Lauwersoog0919","Lauwersoog","09","19",5.1466666666666674,14.246666666666666]
["Lauwersoog0920","Lauwersoog","09","20",5.5333333333333341,14.506666666666668]
["Lauwersoog0921","Lauwersoog","09","21",6.1133333333333333,14.679999999999998]
["Lauwersoog0922","Lauwersoog","09","22",6.833333333333333,15.153333333333334]
["Lauwersoog0923","Lauwersoog","09","23",6.0000000000000018,14.359999999999998]
["Lauwersoog0924","Lauwersoog","09","24",5.9999999999999991,14.120000000000001]
["Lauwersoog0925","Lauwersoog","09","25",5.1400000000000006,14]
["Lauwersoog0926","Lauwersoog","09","26",4.8866666666666658,13.813333333333331]
["Lauwersoog0927","Lauwersoog","09","27",4.3133333333333335,13.846666666666669]
["Lauwersoog0928","Lauwersoog","09","28",5.5866666666666669,14.206666666666667]
["Lauwersoog0929","Lauwersoog","09","29",5.5999999999999988,14.086666666666668]
["Lauwersoog0930","Lauwersoog","09","30",4.9399999999999995,13.700000000000001]
["Lauwersoog1001","Lauwersoog","10","01",5.5199999999999987,13.586666666666668]
["Lauwersoog1002","Lauwersoog","10","02",5.3400000000000007,13.426666666666668]
["Lauwersoog1003","Lauwersoog","10","03",5.7266666666666657,13.846666666666668]
["Lauwersoog1004","Lauwersoog","10","04",6.6333333333333337,13.673333333333334]
["Lauwersoog1005","Lauwersoog","10","05",6.0466666666666669,13.100000000000001]
["Lauwersoog1006","Lauwersoog","10","06",6.3000000000000007,12.786666666666665]
["Lauwersoog1007","Lauwersoog","10","07",6.62,12.399999999999999]
["Lauwersoog1008","Lauwersoog","10","08",6.2733333333333352,12.113333333333335]
["Lauwersoog1009","Lauwersoog","10","09",6.0133333333333345,12.079999999999997]
["Lauwersoog1010","Lauwersoog","10","10",6.4733333333333327,11.659999999999998]
["Lauwersoog1011","Lauwersoog","10","11",6.9133333333333331,11.780000000000003]
["Lauwersoog1012","Lauwersoog","10","12",5.8933333333333335,11.66]
["Lauwersoog1013","Lauwersoog","10","13",4.873333333333334,11.406666666666666]
["Lauwersoog1014","Lauwersoog","10","14",5.3533333333333344,10.773333333333333]
["Lauwersoog1015","Lauwersoog","10","15",5.4466666666666672,10.886666666666665]
["Lauwersoog1016","Lauwersoog","10","16",6.7066666666666661,10.786666666666665]
["Lauwersoog1017","Lauwersoog","10","17",5.9666666666666677,10.406666666666666]
["Lauwersoog1018","Lauwersoog","10","18",5.833333333333333,10.533333333333333]
["Lauwersoog1019","Lauwersoog","10","19",5.5666666666666673,10.793333333333335]
["Lauwersoog1020","Lauwersoog","10","20",6.2666666666666657,10.559999999999999]
["Lauwersoog1021","Lauwersoog","10","21",6.7399999999999993,10.533333333333331]
["Lauwersoog1022","Lauwersoog","10","22",6.28,10.726666666666667]
["Lauwersoog1023","Lauwersoog","10","23",6.3933333333333344,10.586666666666666]
["Lauwersoog1024","Lauwersoog","10","24",6.6133333333333333,10.373333333333333]
["Lauwersoog1025","Lauwersoog","10","25",7.1800000000000006,10.906666666666666]
["Lauwersoog1026","Lauwersoog","10","26",6.3933333333333326,10.493333333333334]
["Lauwersoog1027","Lauwersoog","10","27",6.3666666666666654,10.193333333333333]
["Lauwersoog1028","Lauwersoog","10","28",6.34,10.413333333333332]
["Lauwersoog1029","Lauwersoog","10","29",5.8866666666666667,10]
["Lauwersoog1030","Lauwersoog","10","30",5.4333333333333336,10.18]
["Lauwersoog1031","Lauwersoog","10","31",6.2333333333333334,9.8866666666666649]
["Lauwersoog1101","Lauwersoog","11","01",6.5133333333333336,9.879999999999999]
["Lauwersoog1102","Lauwersoog","11","02",6.2333333333333334,9.6599999999999984]
["Lauwersoog1103","Lauwersoog","11","03",6.753333333333333,9.7800000000000011]
["Lauwersoog1104","Lauwersoog","11","04",5.6400000000000015,9.7266666666666666]
["Lauwersoog1105","Lauwersoog","11","05",6.166666666666667,8.7466666666666679]
["Lauwersoog1106","Lauwersoog","11","06",6.8933333333333326,8.8666666666666671]
["Lauwersoog1107","Lauwersoog","11","07",6.5866666666666678,8.7800000000000011]
["Lauwersoog1108","Lauwersoog","11","08",6.6733333333333329,7.8]
["Lauwersoog1109","Lauwersoog","11","09",7.6466666666666665,7.4666666666666659]
["Lauwersoog1110","Lauwersoog","11","10",5.9599999999999991,7.4000000000000012]
["Lauwersoog1111","Lauwersoog","11","11",6.7799999999999994,7.4066666666666663]
["Lauwersoog1112","Lauwersoog","11","12",7.3466666666666667,7.626666666666666]
["Lauwersoog1113","Lauwersoog","11","13",5.8999999999999995,7.88]
["Lauwersoog1114","Lauwersoog","11","14",5.8999999999999995,7.706666666666667]
["Lauwersoog1115","Lauwersoog","11","15",5.3199999999999994,7.3199999999999994]
["Lauwersoog1116","Lauwersoog","11","16",5.3599999999999994,7.1333333333333346]
["Lauwersoog1117","Lauwersoog","11","17",5.3199999999999985,7.3199999999999994]
["Lauwersoog1118","Lauwersoog","11","18",5.92,7.1866666666666683]
["Lauwersoog1119","Lauwersoog","11","19",5.6,6.8466666666666667]
["Lauwersoog1120","Lauwersoog","11","20",6.1999999999999993,6.5733333333333341]
["Lauwersoog1121","Lauwersoog","11","21",6.4066666666666654,6.02]
["Lauwersoog1122","Lauwersoog","11","22",7.2133333333333329,6.6666666666666661]
["Lauwersoog1123","Lauwersoog","11","23",6.373333333333334,6.7733333333333317]
["Lauwersoog1124","Lauwersoog","11","24",6.0933333333333337,6.3266666666666662]
["Lauwersoog1125","Lauwersoog","11","25",6.6733333333333338,6.3999999999999995]
["Lauwersoog1126","Lauwersoog","11","26",6.3199999999999985,6.04]
["Lauwersoog1127","Lauwersoog","11","27",5.5666666666666664,5.7933333333333339]
["Lauwersoog1128","Lauwersoog","11","28",5.4399999999999995,5.6533333333333333]
["Lauwersoog1129","Lauwersoog","11","29",6.0933333333333337,5.6733333333333338]
["Lauwersoog1130","Lauwersoog","11","30",5.3533333333333344,5.1400000000000006]
["Lauwersoog1201","Lauwersoog","12","01",6.8200000000000012,5.3600000000000012]
["Lauwersoog1202","Lauwersoog","12","02",5.333333333333333,4.88]
["Lauwersoog1203","Lauwersoog","12","03",5.873333333333334,4.8866666666666676]
["Lauwersoog1204","Lauwersoog","12","04",6.72,5.2066666666666661]
["Lauwersoog1205","Lauwersoog","12","05",7.36,5.9133333333333313]
["Lauwersoog1206","Lauwersoog","12","06",7.1933333333333334,5.5066666666666659]
["Lauwersoog1207","Lauwersoog","12","07",6.4666666666666668,4.206666666666667]
["Lauwersoog1208","Lauwersoog","12","08",5.9133333333333331,3.6133333333333324]
["Lauwersoog1209","Lauwersoog","12","09",6.4466666666666672,3.62]
["Lauwersoog1210","Lauwersoog","12","10",6.126666666666666,3.5333333333333337]
["Lauwersoog1211","Lauwersoog","12","11",6.9399999999999986,4.3199999999999994]
["Lauwersoog1212","Lauwersoog","12","12",6.0733333333333333,4.1466666666666665]
["Lauwersoog1213","Lauwersoog","12","13",6.3133333333333335,3.3]
["Lauwersoog1214","Lauwersoog","12","14",6.8000000000000007,2.9200000000000004]
["Lauwersoog1215","Lauwersoog","12","15",7.6666666666666661,4.04]
["Lauwersoog1216","Lauwersoog","12","16",6.9066666666666663,3.726666666666667]
["Lauwersoog1217","Lauwersoog","12","17",5.9133333333333349,3.4666666666666668]
["Lauwersoog1218","Lauwersoog","12","18",5.7866666666666653,3.1866666666666665]
["Lauwersoog1219","Lauwersoog","12","19",6.1800000000000006,2.7466666666666666]
["Lauwersoog1220","Lauwersoog","12","20",7.1533333333333315,2.8933333333333335]
["Lauwersoog1221","Lauwersoog","12","21",6.8533333333333353,2.2999999999999998]
["Lauwersoog1222","Lauwersoog","12","22",6.4866666666666664,2.92]
["Lauwersoog1223","Lauwersoog","12","23",6.879999999999999,3.9599999999999995]
["Lauwersoog1224","Lauwersoog","12","24",7.8733333333333331,4.5133333333333336]
["Lauwersoog1225","Lauwersoog","12","25",6.9999999999999991,4.6800000000000006]
["Lauwersoog1226","Lauwersoog","12","26",5.9000000000000012,3.2933333333333326]
["Lauwersoog1227","Lauwersoog","12","27",6.9533333333333331,3.12]
["Lauwersoog1228","Lauwersoog","12","28",6.9866666666666672,3.4533333333333336]
["Lauwersoog1229","Lauwersoog","12","29",6.4,2.8066666666666666]
["Lauwersoog1230","Lauwersoog","12","30",7.4466666666666672,2.7866666666666671]
["Lauwersoog1231","Lauwersoog","12","31",6.4799999999999995,3.1933333333333338]
["Leeuwarden0101","Leeuwarden","01","01",5.246666666666667,3.4400000000000004]
["Leeuwarden0102","Leeuwarden","01","02",4.7133333333333338,3.2599999999999993]
["Leeuwarden0103","Leeuwarden","01","03",5.6733333333333329,2.94]
["Leeuwarden0104","Leeuwarden","01","04",6.206666666666667,3.3933333333333331]
["Leeuwarden0105","Leeuwarden","01","05",5.5666666666666664,3.253333333333333]
["Leeuwarden0106","Leeuwarden","01","06",5.126666666666666,3.6333333333333337]
["Leeuwarden0107","Leeuwarden","01","07",5.293333333333333,3.9533333333333331]
["Leeuwarden0108","Leeuwarden","01","08",5.7066666666666661,3.6199999999999997]
["Leeuwarden0109","Leeuwarden","01","09",5.5266666666666664,3.3066666666666662]
["Leeuwarden0110","Leeuwarden","01","10",5.8066666666666675,2.9666666666666668]
["Leeuwarden0111","Leeuwarden","01","11",5.9666666666666668,3.6933333333333329]
["Leeuwarden0112","Leeuwarden","01","12",5.7266666666666657,3.313333333333333]
["Leeuwarden0113","Leeuwarden","01","13",5.9933333333333314,3.3866666666666663]
["Leeuwarden0114","Leeuwarden","01","14",4.9266666666666659,3.1933333333333338]
["Leeuwarden0115","Leeuwarden","01","15",5.04,2.6666666666666661]
["Leeuwarden0116","Leeuwarden","01","16",5.1866666666666665,2.8533333333333326]
["Leeuwarden0117","Leeuwarden","01","17",5.7199999999999989,3.5133333333333328]
["Leeuwarden0118","Leeuwarden","01","18",5.64,3.686666666666667]
["Leeuwarden0119","Leeuwarden","01","19",6.0266666666666673,4.22]
["Leeuwarden0120","Leeuwarden","01","20",6.4266666666666659,4.12]
["Leeuwarden0121","Leeuwarden","01","21",5.8533333333333344,3.5200000000000005]
["Leeuwarden0122","Leeuwarden","01","22",5.7933333333333339,2.5133333333333336]
["Leeuwarden0123","Leeuwarden","01","23",5.1866666666666674,2.2333333333333334]
["Leeuwarden0124","Leeuwarden","01","24",4.7066666666666661,2.06]
["Leeuwarden0125","Leeuwarden","01","25",5.0066666666666668,1.6733333333333331]
["Leeuwarden0126","Leeuwarden","01","26",5.5266666666666664,2.2066666666666674]
["Leeuwarden0127","Leeuwarden","01","27",5.12,2.8400000000000003]
["Leeuwarden0128","Leeuwarden","01","28",5.8333333333333339,3.0066666666666659]
["Leeuwarden0129","Leeuwarden","01","29",5.4933333333333332,2.5133333333333332]
["Leeuwarden0130","Leeuwarden","01","30",5.3933333333333335,2.9266666666666667]
["Leeuwarden0131","Leeuwarden","01","31",6.5600000000000014,2.8333333333333339]
["Leeuwarden0201","Leeuwarden","02","01",6.1599999999999993,2.813333333333333]
["Leeuwarden0202","Leeuwarden","02","02",6.4333333333333327,3.5266666666666664]
["Leeuwarden0203","Leeuwarden","02","03",5.58,3.6066666666666665]
["Leeuwarden0204","Leeuwarden","02","04",6.16,3.7466666666666666]
["Leeuwarden0205","Leeuwarden","02","05",6.3266666666666671,4.3466666666666667]
["Leeuwarden0206","Leeuwarden","02","06",5.4266666666666667,4.16]
["Leeuwarden0207","Leeuwarden","02","07",5.7800000000000011,3.5799999999999992]
["Leeuwarden0208","Leeuwarden","02","08",5.9866666666666664,3.0733333333333324]
["Leeuwarden0209","Leeuwarden","02","09",5.6400000000000015,2.9666666666666663]
["Leeuwarden0210","Leeuwarden","02","10",5.7333333333333334,2.6066666666666669]
["Leeuwarden0211","Leeuwarden","02","11",4.9666666666666668,2.7933333333333334]
["Leeuwarden0212","Leeuwarden","02","12",5.52,2.88]
["Leeuwarden0213","Leeuwarden","02","13",4.5866666666666678,3.0333333333333332]
["Leeuwarden0214","Leeuwarden","02","14",4.3733333333333331,2.4933333333333332]
["Leeuwarden0215","Leeuwarden","02","15",4.6866666666666665,2.7600000000000002]
["Leeuwarden0216","Leeuwarden","02","16",4.3,2.6866666666666665]
["Leeuwarden0217","Leeuwarden","02","17",3.7333333333333334,2.1933333333333334]
["Leeuwarden0218","Leeuwarden","02","18",4.26,2.8933333333333331]
["Leeuwarden0219","Leeuwarden","02","19",5.2133333333333338,2.7266666666666666]
["Leeuwarden0220","Leeuwarden","02","20",5.4133333333333331,2.6]
["Leeuwarden0221","Leeuwarden","02","21",5.4333333333333336,2.6266666666666669]
["Leeuwarden0222","Leeuwarden","02","22",6.4333333333333327,3.3066666666666653]
["Leeuwarden0223","Leeuwarden","02","23",5.953333333333334,3.4533333333333336]
["Leeuwarden0224","Leeuwarden","02","24",5.1933333333333325,3.9400000000000004]
["Leeuwarden0225","Leeuwarden","02","25",5.0333333333333341,4.0733333333333333]
["Leeuwarden0226","Leeuwarden","02","26",5.6733333333333329,4.4666666666666659]
["Leeuwarden0227","Leeuwarden","02","27",5.4666666666666668,3.6466666666666661]
["Leeuwarden0228","Leeuwarden","02","28",4.8133333333333326,4.1533333333333333]
["Leeuwarden0229","Leeuwarden","02","29",5.6499999999999995,4.5999999999999996]
["Leeuwarden0301","Leeuwarden","03","01",5.4866666666666672,3.9666666666666668]
["Leeuwarden0302","Leeuwarden","03","02",5.2866666666666671,3.4133333333333336]
["Leeuwarden0303","Leeuwarden","03","03",4.7733333333333325,2.92]
["Leeuwarden0304","Leeuwarden","03","04",5.0466666666666677,3.0733333333333328]
["Leeuwarden0305","Leeuwarden","03","05",4.753333333333333,4.3199999999999994]
["Leeuwarden0306","Leeuwarden","03","06",5.8199999999999994,4.6599999999999993]
["Leeuwarden0307","Leeuwarden","03","07",5.3266666666666671,4.96]
["Leeuwarden0308","Leeuwarden","03","08",6.0333333333333323,5.52]
["Leeuwarden0309","Leeuwarden","03","09",6.3533333333333335,5.44]
["Leeuwarden0310","Leeuwarden","03","10",6.2133333333333338,5.3200000000000012]
["Leeuwarden0311","Leeuwarden","03","11",6.2866666666666653,5.4]
["Leeuwarden0312","Leeuwarden","03","12",4.953333333333334,5.24]
["Leeuwarden0313","Leeuwarden","03","13",4.3066666666666675,4.8999999999999995]
["Leeuwarden0314","Leeuwarden","03","14",5.04,5.0599999999999996]
["Leeuwarden0315","Leeuwarden","03","15",6.04,5.62]
["Leeuwarden0316","Leeuwarden","03","16",5.6133333333333333,6.4466666666666672]
["Leeuwarden0317","Leeuwarden","03","17",5.76,6.206666666666667]
["Leeuwarden0318","Leeuwarden","03","18",5.5133333333333345,5.7933333333333339]
["Leeuwarden0319","Leeuwarden","03","19",5.3666666666666654,4.9999999999999991]
["Leeuwarden0320","Leeuwarden","03","20",4.9399999999999995,5.5333333333333332]
["Leeuwarden0321","Leeuwarden","03","21",4.84,5.2733333333333325]
["Leeuwarden0322","Leeuwarden","03","22",4.9800000000000013,5.0933333333333337]
["Leeuwarden0323","Leeuwarden","03","23",4.92,5.2]
["Leeuwarden0324","Leeuwarden","03","24",4.7399999999999993,5.9399999999999995]
["Leeuwarden0325","Leeuwarden","03","25",4.5,5.8533333333333344]
["Leeuwarden0326","Leeuwarden","03","26",4.1933333333333334,5.626666666666666]
["Leeuwarden0327","Leeuwarden","03","27",5.0133333333333336,6.06]
["Leeuwarden0328","Leeuwarden","03","28",5.1599999999999993,6.5333333333333332]
["Leeuwarden0329","Leeuwarden","03","29",4.5,6.9133333333333322]
["Leeuwarden0330","Leeuwarden","03","30",4.96,7.6799999999999988]
["Leeuwarden0331","Leeuwarden","03","31",5.1133333333333333,7.6466666666666665]
["Leeuwarden0401","Leeuwarden","04","01",5.1799999999999988,8.0266666666666673]
["Leeuwarden0402","Leeuwarden","04","02",5.3200000000000021,9.3866666666666649]
["Leeuwarden0403","Leeuwarden","04","03",5.2533333333333339,8.759999999999998]
["Leeuwarden0404","Leeuwarden","04","04",5.62,7.6]
["Leeuwarden0405","Leeuwarden","04","05",5.96,6.8866666666666658]
["Leeuwarden0406","Leeuwarden","04","06",5.0266666666666673,7.26]
["Leeuwarden0407","Leeuwarden","04","07",4.4466666666666672,6.98]
["Leeuwarden0408","Leeuwarden","04","08",4.8666666666666663,6.2733333333333343]
["Leeuwarden0409","Leeuwarden","04","09",4.5333333333333332,6.7466666666666661]
["Leeuwarden0410","Leeuwarden","04","10",4.1733333333333329,7.48]
["Leeuwarden0411","Leeuwarden","04","11",3.8266666666666667,7.666666666666667]
["Leeuwarden0412","Leeuwarden","04","12",4.5066666666666668,7.7266666666666675]
["Leeuwarden0413","Leeuwarden","04","13",4.3733333333333331,8.0933333333333319]
["Leeuwarden0414","Leeuwarden","04","14",4.4133333333333322,8.6666666666666643]
["Leeuwarden0415","Leeuwarden","04","15",4.24,9.7133333333333347]
["Leeuwarden0416","Leeuwarden","04","16",4.206666666666667,9.2933333333333312]
["Leeuwarden0417","Leeuwarden","04","17",4.8000000000000007,9.08]
["Leeuwarden0418","Leeuwarden","04","18",5.6066666666666665,8.9466666666666672]
["Leeuwarden0419","Leeuwarden","04","19",4.9800000000000004,8.7266666666666683]
["Leeuwarden0420","Leeuwarden","04","20",4.166666666666667,9.2333333333333307]
["Leeuwarden0421","Leeuwarden","04","21",3.7933333333333334,9.84]
["Leeuwarden0422","Leeuwarden","04","22",3.8066666666666662,9.9666666666666668]
["Leeuwarden0423","Leeuwarden","04","23",3.44,10.326666666666664]
["Leeuwarden0424","Leeuwarden","04","24",3.58,12.146666666666667]
["Leeuwarden0425","Leeuwarden","04","25",4.0400000000000009,12.959999999999999]
["Leeuwarden0426","Leeuwarden","04","26",4.22,11.666666666666666]
["Leeuwarden0427","Leeuwarden","04","27",4.6866666666666665,11.139999999999997]
["Leeuwarden0428","Leeuwarden","04","28",4.6000000000000005,11.46]
["Leeuwarden0429","Leeuwarden","04","29",4.8533333333333326,11.300000000000002]
["Leeuwarden0430","Leeuwarden","04","30",4.58,11.193333333333333]
["Leeuwarden0501","Leeuwarden","05","01",4.7933333333333339,10.766666666666667]
["Leeuwarden0502","Leeuwarden","05","02",4.6533333333333333,10.346666666666668]
["Leeuwarden0503","Leeuwarden","05","03",4.4866666666666664,10.353333333333333]
["Leeuwarden0504","Leeuwarden","05","04",4.953333333333334,10.780000000000001]
["Leeuwarden0505","Leeuwarden","05","05",4.7666666666666666,11.34]
["Leeuwarden0506","Leeuwarden","05","06",4.8266666666666662,12.033333333333335]
["Leeuwarden0507","Leeuwarden","05","07",4.8333333333333339,12.566666666666668]
["Leeuwarden0508","Leeuwarden","05","08",4.8666666666666663,12.673333333333334]
["Leeuwarden0509","Leeuwarden","05","09",4.0266666666666673,13.093333333333335]
["Leeuwarden0510","Leeuwarden","05","10",4.72,13.5]
["Leeuwarden0511","Leeuwarden","05","11",4.9933333333333341,11.926666666666668]
["Leeuwarden0512","Leeuwarden","05","12",5.04,11.559999999999999]
["Leeuwarden0513","Leeuwarden","05","13",4.4466666666666681,11.98]
["Leeuwarden0514","Leeuwarden","05","14",4.8600000000000003,11.46]
["Leeuwarden0515","Leeuwarden","05","15",4.1866666666666665,11.719999999999999]
["Leeuwarden0516","Leeuwarden","05","16",4.333333333333333,11.733333333333336]
["Leeuwarden0517","Leeuwarden","05","17",3.8800000000000003,11.413333333333334]
["Leeuwarden0518","Leeuwarden","05","18",4.7333333333333334,12.166666666666668]
["Leeuwarden0519","Leeuwarden","05","19",4.3133333333333335,12.293333333333333]
["Leeuwarden0520","Leeuwarden","05","20",3.873333333333334,13.133333333333335]
["Leeuwarden0521","Leeuwarden","05","21",4.2066666666666661,13.24]
["Leeuwarden0522","Leeuwarden","05","22",4.8066666666666666,13.293333333333333]
["Leeuwarden0523","Leeuwarden","05","23",4.2733333333333325,13.433333333333334]
["Leeuwarden0524","Leeuwarden","05","24",4.5266666666666655,13.139999999999999]
["Leeuwarden0525","Leeuwarden","05","25",4.5466666666666669,13.013333333333332]
["Leeuwarden0526","Leeuwarden","05","26",5.0266666666666673,13.233333333333331]
["Leeuwarden0527","Leeuwarden","05","27",4.7,13.573333333333334]
["Leeuwarden0528","Leeuwarden","05","28",4.8733333333333331,13.606666666666667]
["Leeuwarden0529","Leeuwarden","05","29",4.7333333333333334,13.213333333333335]
["Leeuwarden0530","Leeuwarden","05","30",3.7666666666666662,13.793333333333335]
["Leeuwarden0531","Leeuwarden","05","31",4.3866666666666676,12.96]
["Leeuwarden0601","Leeuwarden","06","01",3.9799999999999991,13.513333333333339]
["Leeuwarden0602","Leeuwarden","06","02",4.3933333333333326,14.306666666666668]
["Leeuwarden0603","Leeuwarden","06","03",4.5066666666666659,14.126666666666667]
["Leeuwarden0604","Leeuwarden","06","04",4.5333333333333332,14.22]
["Leeuwarden0605","Leeuwarden","06","05",4.0733333333333333,13.740000000000002]
["Leeuwarden0606","Leeuwarden","06","06",3.9466666666666668,14.446666666666667]
["Leeuwarden0607","Leeuwarden","06","07",3.9666666666666668,14.893333333333338]
["Leeuwarden0608","Leeuwarden","06","08",3.52,15.58666666666667]
["Leeuwarden0609","Leeuwarden","06","09",3.9866666666666668,15.75333333333333]
["Leeuwarden0610","Leeuwarden","06","10",3.6066666666666669,15.54666666666667]
["Leeuwarden0611","Leeuwarden","06","11",4.3066666666666675,14.893333333333334]
["Leeuwarden0612","Leeuwarden","06","12",4.4000000000000004,14.626666666666665]
["Leeuwarden0613","Leeuwarden","06","13",4.34,14.500000000000002]
["Leeuwarden0614","Leeuwarden","06","14",3.8733333333333335,14.386666666666665]
["Leeuwarden0615","Leeuwarden","06","15",4.34,14.513333333333334]
["Leeuwarden0616","Leeuwarden","06","16",4.3466666666666667,14.213333333333333]
["Leeuwarden0617","Leeuwarden","06","17",4.1999999999999993,15.699999999999998]
["Leeuwarden0618","Leeuwarden","06","18",4.1266666666666669,16.213333333333331]
["Leeuwarden0619","Leeuwarden","06","19",4.7399999999999993,16.240000000000002]
["Leeuwarden0620","Leeuwarden","06","20",4.6266666666666678,16.18]
["Leeuwarden0621","Leeuwarden","06","21",4.0199999999999996,15.306666666666667]
["Leeuwarden0622","Leeuwarden","06","22",4.8333333333333339,15.533333333333331]
["Leeuwarden0623","Leeuwarden","06","23",4.7466666666666653,15.646666666666667]
["Leeuwarden0624","Leeuwarden","06","24",4.5933333333333328,15.1]
["Leeuwarden0625","Leeuwarden","06","25",4.5799999999999992,15.06]
["Leeuwarden0626","Leeuwarden","06","26",4.3600000000000003,15.626666666666667]
["Leeuwarden0627","Leeuwarden","06","27",4.5,16.36]
["Leeuwarden0628","Leeuwarden","06","28",4.3666666666666663,16.513333333333332]
["Leeuwarden0629","Leeuwarden","06","29",4.34,15.69333333333333]
["Leeuwarden0630","Leeuwarden","06","30",3.839999999999999,16.073333333333334]
["Leeuwarden0701","Leeuwarden","07","01",4.1533333333333333,16.193333333333332]
["Leeuwarden0702","Leeuwarden","07","02",4.04,17.72666666666667]
["Leeuwarden0703","Leeuwarden","07","03",4.0133333333333328,17.533333333333335]
["Leeuwarden0704","Leeuwarden","07","04",4.1866666666666665,17.893333333333334]
["Leeuwarden0705","Leeuwarden","07","05",3.48,17.833333333333332]
["Leeuwarden0706","Leeuwarden","07","06",4.0533333333333328,16.926666666666666]
["Leeuwarden0707","Leeuwarden","07","07",4.1533333333333333,16.739999999999998]
["Leeuwarden0708","Leeuwarden","07","08",4.1066666666666665,16.7]
["Leeuwarden0709","Leeuwarden","07","09",4.4333333333333336,16.786666666666669]
["Leeuwarden0710","Leeuwarden","07","10",4.22,17.146666666666665]
["Leeuwarden0711","Leeuwarden","07","11",4.7866666666666662,16.513333333333335]
["Leeuwarden0712","Leeuwarden","07","12",4.4000000000000004,15.953333333333335]
["Leeuwarden0713","Leeuwarden","07","13",4.0533333333333337,16.266666666666666]
["Leeuwarden0714","Leeuwarden","07","14",3.9466666666666659,17.153333333333332]
["Leeuwarden0715","Leeuwarden","07","15",4.5733333333333341,17.233333333333338]
["Leeuwarden0716","Leeuwarden","07","16",3.8666666666666663,17.499999999999996]
["Leeuwarden0717","Leeuwarden","07","17",4.18,17.353333333333332]
["Leeuwarden0718","Leeuwarden","07","18",4.6666666666666679,17.153333333333332]
["Leeuwarden0719","Leeuwarden","07","19",4.3133333333333335,18.113333333333337]
["Leeuwarden0720","Leeuwarden","07","20",4.2399999999999993,17.426666666666666]
["Leeuwarden0721","Leeuwarden","07","21",4.3733333333333331,17.446666666666665]
["Leeuwarden0722","Leeuwarden","07","22",4.1533333333333342,17.553333333333335]
["Leeuwarden0723","Leeuwarden","07","23",3.9533333333333336,17.786666666666669]
["Leeuwarden0724","Leeuwarden","07","24",4.0599999999999996,17.38]
["Leeuwarden0725","Leeuwarden","07","25",3.4599999999999995,17.54666666666667]
["Leeuwarden0726","Leeuwarden","07","26",3.6466666666666665,17.966666666666672]
["Leeuwarden0727","Leeuwarden","07","27",2.94,18.579999999999998]
["Leeuwarden0728","Leeuwarden","07","28",3.2333333333333334,18.779999999999998]
["Leeuwarden0729","Leeuwarden","07","29",3.5466666666666664,18.62]
["Leeuwarden0730","Leeuwarden","07","30",4.0200000000000005,17.600000000000001]
["Leeuwarden0731","Leeuwarden","07","31",3.5933333333333333,17.833333333333332]
["Leeuwarden0801","Leeuwarden","08","01",3.2733333333333334,18.353333333333335]
["Leeuwarden0802","Leeuwarden","08","02",3.3599999999999994,18.366666666666667]
["Leeuwarden0803","Leeuwarden","08","03",3.3466666666666667,17.54]
["Leeuwarden0804","Leeuwarden","08","04",3.6066666666666674,17.713333333333328]
["Leeuwarden0805","Leeuwarden","08","05",3.333333333333333,18.446666666666665]
["Leeuwarden0806","Leeuwarden","08","06",3.68,18.733333333333331]
["Leeuwarden0807","Leeuwarden","08","07",3.5933333333333328,18.06666666666667]
["Leeuwarden0808","Leeuwarden","08","08",4.4666666666666668,17.506666666666668]
["Leeuwarden0809","Leeuwarden","08","09",4.1266666666666669,17.293333333333337]
["Leeuwarden0810","Leeuwarden","08","10",4.126666666666666,17.073333333333334]
["Leeuwarden0811","Leeuwarden","08","11",3.8133333333333335,16.966666666666665]
["Leeuwarden0812","Leeuwarden","08","12",3.7866666666666671,16.866666666666664]
["Leeuwarden0813","Leeuwarden","08","13",4.2133333333333338,17.013333333333332]
["Leeuwarden0814","Leeuwarden","08","14",4.046666666666666,17.740000000000002]
["Leeuwarden0815","Leeuwarden","08","15",4.4466666666666672,18.16]
["Leeuwarden0816","Leeuwarden","08","16",3.4933333333333327,17.526666666666664]
["Leeuwarden0817","Leeuwarden","08","17",3.746666666666667,17.726666666666667]
["Leeuwarden0818","Leeuwarden","08","18",4.1000000000000005,18.579999999999998]
["Leeuwarden0819","Leeuwarden","08","19",4.246666666666667,18.373333333333338]
["Leeuwarden0820","Leeuwarden","08","20",3.7066666666666666,17.433333333333334]
["Leeuwarden0821","Leeuwarden","08","21",3.5066666666666673,16.833333333333336]
["Leeuwarden0822","Leeuwarden","08","22",3.5133333333333332,16.753333333333337]
["Leeuwarden0823","Leeuwarden","08","23",3.3733333333333331,16.653333333333332]
["Leeuwarden0824","Leeuwarden","08","24",3.5666666666666673,17.006666666666668]
["Leeuwarden0825","Leeuwarden","08","25",3.6333333333333333,17.113333333333333]
["Leeuwarden0826","Leeuwarden","08","26",4.3066666666666666,16.613333333333333]
["Leeuwarden0827","Leeuwarden","08","27",4.1533333333333333,16.2]
["Leeuwarden0828","Leeuwarden","08","28",3.9933333333333336,15.633333333333335]
["Leeuwarden0829","Leeuwarden","08","29",3.8666666666666671,15.213333333333335]
["Leeuwarden0830","Leeuwarden","08","30",4.16,15.780000000000001]
["Leeuwarden0831","Leeuwarden","08","31",4.379999999999999,15.98]
["Leeuwarden0901","Leeuwarden","09","01",3.9200000000000004,15.333333333333334]
["Leeuwarden0902","Leeuwarden","09","02",3.9000000000000004,15.700000000000001]
["Leeuwarden0903","Leeuwarden","09","03",4.293333333333333,16.013333333333335]
["Leeuwarden0904","Leeuwarden","09","04",4.4933333333333341,15.853333333333333]
["Leeuwarden0905","Leeuwarden","09","05",3.82,16.34]
["Leeuwarden0906","Leeuwarden","09","06",4.6266666666666669,16.626666666666669]
["Leeuwarden0907","Leeuwarden","09","07",4.8466666666666667,15.919999999999998]
["Leeuwarden0908","Leeuwarden","09","08",4.4866666666666664,15.706666666666667]
["Leeuwarden0909","Leeuwarden","09","09",4.1933333333333334,16.053333333333331]
["Leeuwarden0910","Leeuwarden","09","10",4.5600000000000005,15.906666666666666]
["Leeuwarden0911","Leeuwarden","09","11",4.5999999999999996,16.38666666666667]
["Leeuwarden0912","Leeuwarden","09","12",4.4333333333333336,15.706666666666667]
["Leeuwarden0913","Leeuwarden","09","13",4.2600000000000007,15.073333333333331]
["Leeuwarden0914","Leeuwarden","09","14",5.1933333333333325,15.086666666666666]
["Leeuwarden0915","Leeuwarden","09","15",4.3266666666666671,14.493333333333332]
["Leeuwarden0916","Leeuwarden","09","16",4.1666666666666661,14.173333333333334]
["Leeuwarden0917","Leeuwarden","09","17",3.7133333333333329,14.286666666666665]
["Leeuwarden0918","Leeuwarden","09","18",3.6933333333333338,13.753333333333336]
["Leeuwarden0919","Leeuwarden","09","19",3.8666666666666663,13.659999999999998]
["Leeuwarden0920","Leeuwarden","09","20",4.2399999999999993,13.966666666666665]
["Leeuwarden0921","Leeuwarden","09","21",4.38,14.120000000000001]
["Leeuwarden0922","Leeuwarden","09","22",4.7,14.633333333333333]
["Leeuwarden0923","Leeuwarden","09","23",4.0066666666666668,13.819999999999995]
["Leeuwarden0924","Leeuwarden","09","24",4.2400000000000011,13.513333333333332]
["Leeuwarden0925","Leeuwarden","09","25",3.5133333333333336,13.440000000000001]
["Leeuwarden0926","Leeuwarden","09","26",3.4333333333333322,13.259999999999998]
["Leeuwarden0927","Leeuwarden","09","27",3.0133333333333336,13.060000000000002]
["Leeuwarden0928","Leeuwarden","09","28",4.0266666666666664,13.826666666666664]
["Leeuwarden0929","Leeuwarden","09","29",3.9466666666666659,13.673333333333334]
["Leeuwarden0930","Leeuwarden","09","30",3.899999999999999,13.46]
["Leeuwarden1001","Leeuwarden","10","01",4.2866666666666671,13.133333333333333]
["Leeuwarden1002","Leeuwarden","10","02",4.1866666666666665,12.846666666666668]
["Leeuwarden1003","Leeuwarden","10","03",4.58,13.559999999999999]
["Leeuwarden1004","Leeuwarden","10","04",4.5733333333333333,12.986666666666666]
["Leeuwarden1005","Leeuwarden","10","05",4.4133333333333331,12.72]
["Leeuwarden1006","Leeuwarden","10","06",4.793333333333333,12.359999999999998]
["Leeuwarden1007","Leeuwarden","10","07",4.7999999999999989,11.813333333333333]
["Leeuwarden1008","Leeuwarden","10","08",4.2200000000000006,11.293333333333335]
["Leeuwarden1009","Leeuwarden","10","09",4.3599999999999994,11.313333333333333]
["Leeuwarden1010","Leeuwarden","10","10",4.9066666666666672,11.233333333333333]
["Leeuwarden1011","Leeuwarden","10","11",5.42,11.360000000000001]
["Leeuwarden1012","Leeuwarden","10","12",4.2266666666666666,11.066666666666666]
["Leeuwarden1013","Leeuwarden","10","13",3.6533333333333333,10.739999999999998]
["Leeuwarden1014","Leeuwarden","10","14",4.0666666666666664,10.393333333333333]
["Leeuwarden1015","Leeuwarden","10","15",3.9466666666666659,10.373333333333333]
["Leeuwarden1016","Leeuwarden","10","16",4.9800000000000004,10.373333333333335]
["Leeuwarden1017","Leeuwarden","10","17",4.2866666666666662,9.8599999999999977]
["Leeuwarden1018","Leeuwarden","10","18",4.5733333333333341,10.32]
["Leeuwarden1019","Leeuwarden","10","19",4.0333333333333332,10.56]
["Leeuwarden1020","Leeuwarden","10","20",4.7866666666666662,10.386666666666667]
["Leeuwarden1021","Leeuwarden","10","21",5.3,10.393333333333334]
["Leeuwarden1022","Leeuwarden","10","22",5.1066666666666665,10.680000000000001]
["Leeuwarden1023","Leeuwarden","10","23",5.14,10.426666666666666]
["Leeuwarden1024","Leeuwarden","10","24",5.2,10.306666666666668]
["Leeuwarden1025","Leeuwarden","10","25",5.6933333333333325,10.780000000000001]
["Leeuwarden1026","Leeuwarden","10","26",5.3000000000000007,10.366666666666665]
["Leeuwarden1027","Leeuwarden","10","27",5.2133333333333329,10.046666666666665]
["Leeuwarden1028","Leeuwarden","10","28",5.0066666666666659,10.340000000000002]
["Leeuwarden1029","Leeuwarden","10","29",4.58,9.9266666666666659]
["Leeuwarden1030","Leeuwarden","10","30",4.5000000000000009,9.7266666666666648]
["Leeuwarden1031","Leeuwarden","10","31",4.9000000000000004,9.7933333333333312]
["Leeuwarden1101","Leeuwarden","11","01",4.9733333333333336,9.7333333333333325]
["Leeuwarden1102","Leeuwarden","11","02",4.9666666666666659,9.6866666666666674]
["Leeuwarden1103","Leeuwarden","11","03",5.5600000000000005,9.9933333333333341]
["Leeuwarden1104","Leeuwarden","11","04",4.28,9.5200000000000014]
["Leeuwarden1105","Leeuwarden","11","05",4.333333333333333,8.5599999999999987]
["Leeuwarden1106","Leeuwarden","11","06",5.0733333333333333,8.6133333333333333]
["Leeuwarden1107","Leeuwarden","11","07",4.9533333333333331,8.48]
["Leeuwarden1108","Leeuwarden","11","08",5.4666666666666668,7.6933333333333334]
["Leeuwarden1109","Leeuwarden","11","09",5.293333333333333,6.873333333333334]
["Leeuwarden1110","Leeuwarden","11","10",4.5266666666666664,7.133333333333332]
["Leeuwarden1111","Leeuwarden","11","11",5.5733333333333341,7.379999999999999]
["Leeuwarden1112","Leeuwarden","11","12",5.6599999999999993,7.52]
["Leeuwarden1113","Leeuwarden","11","13",4.5133333333333336,7.5266666666666664]
["Leeuwarden1114","Leeuwarden","11","14",4.5200000000000005,7.4066666666666654]
["Leeuwarden1115","Leeuwarden","11","15",4.086666666666666,6.7666666666666657]
["Leeuwarden1116","Leeuwarden","11","16",4.0133333333333328,6.9133333333333331]
["Leeuwarden1117","Leeuwarden","11","17",4.0533333333333337,7.1466666666666647]
["Leeuwarden1118","Leeuwarden","11","18",4.5333333333333332,6.9333333333333336]
["Leeuwarden1119","Leeuwarden","11","19",4.08,6.2733333333333325]
["Leeuwarden1120","Leeuwarden","11","20",4.5599999999999996,6.3133333333333344]
["Leeuwarden1121","Leeuwarden","11","21",5.0866666666666669,5.793333333333333]
["Leeuwarden1122","Leeuwarden","11","22",5.4066666666666672,6.5866666666666678]
["Leeuwarden1123","Leeuwarden","11","23",4.6266666666666669,6.4799999999999995]
["Leeuwarden1124","Leeuwarden","11","24",4.5999999999999996,6.073333333333335]
["Leeuwarden1125","Leeuwarden","11","25",5.26,6.02]
["Leeuwarden1126","Leeuwarden","11","26",4.9333333333333336,5.793333333333333]
["Leeuwarden1127","Leeuwarden","11","27",4.42,5.66]
["Leeuwarden1128","Leeuwarden","11","28",4.3466666666666658,5.4933333333333341]
["Leeuwarden1129","Leeuwarden","11","29",4.673333333333332,5.4799999999999995]
["Leeuwarden1130","Leeuwarden","11","30",4.1399999999999997,5.006666666666665]
["Leeuwarden1201","Leeuwarden","12","01",5.2866666666666653,5.1933333333333334]
["Leeuwarden1202","Leeuwarden","12","02",4.2399999999999993,4.5199999999999996]
["Leeuwarden1203","Leeuwarden","12","03",4.7,4.8266666666666662]
["Leeuwarden1204","Leeuwarden","12","04",5.5400000000000009,5.1866666666666656]
["Leeuwarden1205","Leeuwarden","12","05",5.6933333333333334,5.8800000000000008]
["Leeuwarden1206","Leeuwarden","12","06",5.2533333333333321,5.0666666666666673]
["Leeuwarden1207","Leeuwarden","12","07",5.2,3.7933333333333339]
["Leeuwarden1208","Leeuwarden","12","08",4.753333333333333,3.2]
["Leeuwarden1209","Leeuwarden","12","09",4.9800000000000004,3.2933333333333334]
["Leeuwarden1210","Leeuwarden","12","10",4.6800000000000006,3.04]
["Leeuwarden1211","Leeuwarden","12","11",5.4066666666666672,3.96]
["Leeuwarden1212","Leeuwarden","12","12",4.6466666666666656,3.7866666666666666]
["Leeuwarden1213","Leeuwarden","12","13",5.22,3.0466666666666664]
["Leeuwarden1214","Leeuwarden","12","14",5.34,2.6466666666666665]
["Leeuwarden1215","Leeuwarden","12","15",5.746666666666667,3.8200000000000003]
["Leeuwarden1216","Leeuwarden","12","16",5.0733333333333333,3.32]
["Leeuwarden1217","Leeuwarden","12","17",4.2266666666666666,3.0066666666666668]
["Leeuwarden1218","Leeuwarden","12","18",3.9066666666666663,2.52]
["Leeuwarden1219","Leeuwarden","12","19",4.5,2.1533333333333333]
["Leeuwarden1220","Leeuwarden","12","20",5.4333333333333336,2.7733333333333334]
["Leeuwarden1221","Leeuwarden","12","21",5.3133333333333335,2.3199999999999998]
["Leeuwarden1222","Leeuwarden","12","22",5.120000000000001,3.0733333333333333]
["Leeuwarden1223","Leeuwarden","12","23",5.7600000000000007,3.9133333333333331]
["Leeuwarden1224","Leeuwarden","12","24",6.0400000000000009,4.8200000000000012]
["Leeuwarden1225","Leeuwarden","12","25",5.2066666666666661,4.5066666666666659]
["Leeuwarden1226","Leeuwarden","12","26",4.5866666666666669,3.0333333333333332]
["Leeuwarden1227","Leeuwarden","12","27",5.4933333333333314,2.9399999999999995]
["Leeuwarden1228","Leeuwarden","12","28",5.3,3.1400000000000006]
["Leeuwarden1229","Leeuwarden","12","29",5.0799999999999992,2.6600000000000006]
["Leeuwarden1230","Leeuwarden","12","30",5.4600000000000017,2.58]
["Leeuwarden1231","Leeuwarden","12","31",4.9733333333333327,2.8133333333333335]
["Maastricht0101","Maastricht","01","01",5.04,3.68]
["Maastricht0102","Maastricht","01","02",4.9266666666666667,3.253333333333333]
["Maastricht0103","Maastricht","01","03",5.6266666666666669,2.8866666666666672]
["Maastricht0104","Maastricht","01","04",5.7333333333333334,2.94]
["Maastricht0105","Maastricht","01","05",5.22,3.1333333333333337]
["Maastricht0106","Maastricht","01","06",4.8133333333333326,3.48]
["Maastricht0107","Maastricht","01","07",5.0266666666666673,3.8800000000000003]
["Maastricht0108","Maastricht","01","08",5.34,3.5333333333333332]
["Maastricht0109","Maastricht","01","09",4.753333333333333,2.9733333333333336]
["Maastricht0110","Maastricht","01","10",4.3666666666666663,2.813333333333333]
["Maastricht0111","Maastricht","01","11",5.5333333333333323,3.6066666666666669]
["Maastricht0112","Maastricht","01","12",5.26,3.1733333333333338]
["Maastricht0113","Maastricht","01","13",5.2133333333333329,3.8933333333333326]
["Maastricht0114","Maastricht","01","14",4.4666666666666668,3.3999999999999995]
["Maastricht0115","Maastricht","01","15",4.9466666666666681,2.4066666666666663]
["Maastricht0116","Maastricht","01","16",4.7133333333333329,3.0066666666666673]
["Maastricht0117","Maastricht","01","17",5.3133333333333326,4.1133333333333333]
["Maastricht0118","Maastricht","01","18",5.6733333333333329,4.38]
["Maastricht0119","Maastricht","01","19",5.3400000000000007,5.0999999999999996]
["Maastricht0120","Maastricht","01","20",5.66,4.8133333333333326]
["Maastricht0121","Maastricht","01","21",4.6933333333333334,4.04]
["Maastricht0122","Maastricht","01","22",4.4466666666666672,3.54]
["Maastricht0123","Maastricht","01","23",4.5533333333333337,2.64]
["Maastricht0124","Maastricht","01","24",3.7399999999999998,1.9133333333333331]
["Maastricht0125","Maastricht","01","25",4.1333333333333329,1.5733333333333335]
["Maastricht0126","Maastricht","01","26",5.5866666666666669,1.76]
["Maastricht0127","Maastricht","01","27",4.96,2.1066666666666665]
["Maastricht0128","Maastricht","01","28",5.3466666666666649,2.56]
["Maastricht0129","Maastricht","01","29",5.0933333333333328,2.5866666666666664]
["Maastricht0130","Maastricht","01","30",4.5599999999999996,2.6533333333333342]
["Maastricht0131","Maastricht","01","31",5.9333333333333336,2.7333333333333329]
["Maastricht0201","Maastricht","02","01",5.6866666666666674,2.6466666666666669]
["Maastricht0202","Maastricht","02","02",5.5200000000000005,3.0733333333333328]
["Maastricht0203","Maastricht","02","03",4.2399999999999993,3.4133333333333331]
["Maastricht0204","Maastricht","02","04",5.2866666666666671,4.4333333333333336]
["Maastricht0205","Maastricht","02","05",6.1,5.2066666666666661]
["Maastricht0206","Maastricht","02","06",4.8266666666666662,4.9266666666666667]
["Maastricht0207","Maastricht","02","07",5.1999999999999984,3.5466666666666673]
["Maastricht0208","Maastricht","02","08",5.6400000000000006,3.9]
["Maastricht0209","Maastricht","02","09",4.74,3.1533333333333338]
["Maastricht0210","Maastricht","02","10",4.9866666666666664,3.0066666666666668]
["Maastricht0211","Maastricht","02","11",5.2600000000000007,3.78]
["Maastricht0212","Maastricht","02","12",5.0533333333333328,3.6133333333333337]
["Maastricht0213","Maastricht","02","13",3.9933333333333336,2.7866666666666666]
["Maastricht0214","Maastricht","02","14",4.1866666666666665,2.7133333333333329]
["Maastricht0215","Maastricht","02","15",4.6266666666666669,3.3666666666666667]
["Maastricht0216","Maastricht","02","16",4.0333333333333341,3.1466666666666665]
["Maastricht0217","Maastricht","02","17",3.9266666666666672,3.0266666666666668]
["Maastricht0218","Maastricht","02","18",3.8466666666666667,2.8466666666666667]
["Maastricht0219","Maastricht","02","19",4.453333333333334,3.1066666666666669]
["Maastricht0220","Maastricht","02","20",4.5866666666666678,3.1199999999999997]
["Maastricht0221","Maastricht","02","21",4.666666666666667,3.0866666666666669]
["Maastricht0222","Maastricht","02","22",5.4999999999999991,3.6800000000000006]
["Maastricht0223","Maastricht","02","23",4.6266666666666669,3.7800000000000007]
["Maastricht0224","Maastricht","02","24",4.8533333333333344,4.666666666666667]
["Maastricht0225","Maastricht","02","25",4.9000000000000004,4.753333333333333]
["Maastricht0226","Maastricht","02","26",4.9399999999999995,4.6799999999999988]
["Maastricht0227","Maastricht","02","27",5.1533333333333342,4.4066666666666663]
["Maastricht0228","Maastricht","02","28",4.9000000000000012,4.8000000000000007]
["Maastricht0229","Maastricht","02","29",4.6500000000000004,5.5250000000000004]
["Maastricht0301","Maastricht","03","01",4.6733333333333329,4.34]
["Maastricht0302","Maastricht","03","02",4.26,4.0666666666666664]
["Maastricht0303","Maastricht","03","03",4.4666666666666668,3.6000000000000005]
["Maastricht0304","Maastricht","03","04",3.7533333333333334,3.9066666666666672]
["Maastricht0305","Maastricht","03","05",3.82,3.9533333333333331]
["Maastricht0306","Maastricht","03","06",4.833333333333333,4.4933333333333341]
["Maastricht0307","Maastricht","03","07",4.7133333333333338,5.666666666666667]
["Maastricht0308","Maastricht","03","08",4.8,6.6333333333333337]
["Maastricht0309","Maastricht","03","09",5.5533333333333337,7.02]
["Maastricht0310","Maastricht","03","10",5.4133333333333322,6.0666666666666673]
["Maastricht0311","Maastricht","03","11",5.1599999999999993,6.0799999999999983]
["Maastricht0312","Maastricht","03","12",4.206666666666667,5.6466666666666674]
["Maastricht0313","Maastricht","03","13",4.0933333333333328,5.9133333333333349]
["Maastricht0314","Maastricht","03","14",4.1933333333333334,6.0266666666666682]
["Maastricht0315","Maastricht","03","15",4.126666666666666,7.26]
["Maastricht0316","Maastricht","03","16",4.2666666666666666,8.5066666666666677]
["Maastricht0317","Maastricht","03","17",4.293333333333333,7.8600000000000012]
["Maastricht0318","Maastricht","03","18",4.7533333333333321,7.4533333333333331]
["Maastricht0319","Maastricht","03","19",4.2733333333333343,6.4799999999999995]
["Maastricht0320","Maastricht","03","20",4.4399999999999995,6.5133333333333336]
["Maastricht0321","Maastricht","03","21",4.3466666666666667,6.4800000000000013]
["Maastricht0322","Maastricht","03","22",4.3266666666666662,6.8933333333333335]
["Maastricht0323","Maastricht","03","23",3.8133333333333339,7.0133333333333345]
["Maastricht0324","Maastricht","03","24",3.813333333333333,7.5200000000000005]
["Maastricht0325","Maastricht","03","25",4.0400000000000009,7.333333333333333]
["Maastricht0326","Maastricht","03","26",3.9333333333333331,6.9999999999999991]
["Maastricht0327","Maastricht","03","27",3.78,7.7666666666666666]
["Maastricht0328","Maastricht","03","28",4.1866666666666665,8.1933333333333334]
["Maastricht0329","Maastricht","03","29",3.773333333333333,8.5200000000000014]
["Maastricht0330","Maastricht","03","30",3.833333333333333,8.7666666666666639]
["Maastricht0331","Maastricht","03","31",4.24,9.24]
["Maastricht0401","Maastricht","04","01",4.3999999999999995,9.7066666666666688]
["Maastricht0402","Maastricht","04","02",4.3266666666666671,10.606666666666667]
["Maastricht0403","Maastricht","04","03",4.3066666666666666,10.039999999999997]
["Maastricht0404","Maastricht","04","04",4.58,9.1066666666666656]
["Maastricht0405","Maastricht","04","05",4.7866666666666662,7.4733333333333327]
["Maastricht0406","Maastricht","04","06",4.3333333333333321,8.4333333333333336]
["Maastricht0407","Maastricht","04","07",4.0266666666666664,8.3066666666666666]
["Maastricht0408","Maastricht","04","08",3.6533333333333333,7.366666666666668]
["Maastricht0409","Maastricht","04","09",3.8533333333333331,7.953333333333334]
["Maastricht0410","Maastricht","04","10",3.7933333333333339,8.42]
["Maastricht0411","Maastricht","04","11",3.4333333333333327,8.68]
["Maastricht0412","Maastricht","04","12",3.9933333333333336,8.9666666666666686]
["Maastricht0413","Maastricht","04","13",4.3066666666666675,9.3666666666666671]
["Maastricht0414","Maastricht","04","14",3.6733333333333333,10.106666666666664]
["Maastricht0415","Maastricht","04","15",3.8533333333333335,10.62]
["Maastricht0416","Maastricht","04","16",3.6933333333333334,10.28]
["Maastricht0417","Maastricht","04","17",4.0266666666666664,10.433333333333334]
["Maastricht0418","Maastricht","04","18",4.5799999999999992,10.033333333333333]
["Maastricht0419","Maastricht","04","19",3.753333333333333,9.1066666666666656]
["Maastricht0420","Maastricht","04","20",3.6066666666666669,10.206666666666667]
["Maastricht0421","Maastricht","04","21",3.1733333333333329,11.073333333333332]
["Maastricht0422","Maastricht","04","22",2.9733333333333332,11.180000000000001]
["Maastricht0423","Maastricht","04","23",3.0333333333333332,12.020000000000001]
["Maastricht0424","Maastricht","04","24",3.1799999999999997,13.446666666666665]
["Maastricht0425","Maastricht","04","25",3.7,14.446666666666669]
["Maastricht0426","Maastricht","04","26",4.0466666666666669,13.226666666666665]
["Maastricht0427","Maastricht","04","27",4.1399999999999997,12.493333333333334]
["Maastricht0428","Maastricht","04","28",3.72,13.146666666666665]
["Maastricht0429","Maastricht","04","29",4.2600000000000007,12.873333333333333]
["Maastricht0430","Maastricht","04","30",4.0733333333333333,13.246666666666668]
["Maastricht0501","Maastricht","05","01",4.4000000000000004,13.473333333333333]
["Maastricht0502","Maastricht","05","02",3.9666666666666663,13.040000000000003]
["Maastricht0503","Maastricht","05","03",3.773333333333333,12.413333333333334]
["Maastricht0504","Maastricht","05","04",3.8466666666666667,12.080000000000002]
["Maastricht0505","Maastricht","05","05",4.1466666666666665,12.426666666666668]
["Maastricht0506","Maastricht","05","06",3.7866666666666675,12.860000000000003]
["Maastricht0507","Maastricht","05","07",4.2133333333333329,13.493333333333336]
["Maastricht0508","Maastricht","05","08",4.3466666666666676,13.726666666666668]
["Maastricht0509","Maastricht","05","09",3.3866666666666672,14.166666666666668]
["Maastricht0510","Maastricht","05","10",4.0333333333333341,14.973333333333333]
["Maastricht0511","Maastricht","05","11",4.253333333333333,13.806666666666665]
["Maastricht0512","Maastricht","05","12",4.12,12.793333333333333]
["Maastricht0513","Maastricht","05","13",3.5466666666666673,13.22]
["Maastricht0514","Maastricht","05","14",3.5799999999999996,12.82]
["Maastricht0515","Maastricht","05","15",3.2266666666666666,12.826666666666663]
["Maastricht0516","Maastricht","05","16",3.6533333333333333,13.566666666666666]
["Maastricht0517","Maastricht","05","17",3.56,13.093333333333332]
["Maastricht0518","Maastricht","05","18",4.0999999999999996,13.360000000000001]
["Maastricht0519","Maastricht","05","19",3.9533333333333331,14.146666666666667]
["Maastricht0520","Maastricht","05","20",3.7133333333333338,14.613333333333333]
["Maastricht0521","Maastricht","05","21",3.7133333333333334,14.72]
["Maastricht0522","Maastricht","05","22",4.2799999999999994,14.453333333333331]
["Maastricht0523","Maastricht","05","23",3.8466666666666667,14.62]
["Maastricht0524","Maastricht","05","24",3.9,15.346666666666669]
["Maastricht0525","Maastricht","05","25",3.6933333333333334,15.520000000000001]
["Maastricht0526","Maastricht","05","26",3.9933333333333332,15.240000000000002]
["Maastricht0527","Maastricht","05","27",3.9266666666666667,15.126666666666665]
["Maastricht0528","Maastricht","05","28",3.9933333333333332,15.733333333333333]
["Maastricht0529","Maastricht","05","29",3.9866666666666672,14.793333333333333]
["Maastricht0530","Maastricht","05","30",3.2999999999999994,14.726666666666663]
["Maastricht0531","Maastricht","05","31",3.28,14.446666666666667]
["Maastricht0601","Maastricht","06","01",3.1333333333333329,15.153333333333334]
["Maastricht0602","Maastricht","06","02",3.6066666666666665,16.013333333333332]
["Maastricht0603","Maastricht","06","03",3.6400000000000006,16.100000000000001]
["Maastricht0604","Maastricht","06","04",3.88,15.866666666666669]
["Maastricht0605","Maastricht","06","05",3.3733333333333335,15.466666666666667]
["Maastricht0606","Maastricht","06","06",3.42,16.18]
["Maastricht0607","Maastricht","06","07",3.4000000000000004,16.826666666666668]
["Maastricht0608","Maastricht","06","08",3.4533333333333331,17.406666666666663]
["Maastricht0609","Maastricht","06","09",3.7466666666666657,17.426666666666669]
["Maastricht0610","Maastricht","06","10",2.9733333333333336,16.86]
["Maastricht0611","Maastricht","06","11",3.2533333333333334,15.793333333333331]
["Maastricht0612","Maastricht","06","12",3.5866666666666669,15.886666666666665]
["Maastricht0613","Maastricht","06","13",3.3066666666666666,16.32]
["Maastricht0614","Maastricht","06","14",2.9599999999999995,16.893333333333334]
["Maastricht0615","Maastricht","06","15",4.0199999999999996,16.413333333333334]
["Maastricht0616","Maastricht","06","16",3.9466666666666663,16.013333333333332]
["Maastricht0617","Maastricht","06","17",3.6,17.619999999999997]
["Maastricht0618","Maastricht","06","18",3.9266666666666663,18.186666666666667]
["Maastricht0619","Maastricht","06","19",3.746666666666667,17.586666666666666]
["Maastricht0620","Maastricht","06","20",3.2533333333333334,17.399999999999999]
["Maastricht0621","Maastricht","06","21",3.5399999999999996,16.88]
["Maastricht0622","Maastricht","06","22",4.2399999999999993,16.986666666666668]
["Maastricht0623","Maastricht","06","23",4.6066666666666665,17.04]
["Maastricht0624","Maastricht","06","24",4.0866666666666669,17.333333333333332]
["Maastricht0625","Maastricht","06","25",3.5533333333333332,16.986666666666665]
["Maastricht0626","Maastricht","06","26",3.2199999999999998,17.480000000000004]
["Maastricht0627","Maastricht","06","27",3.4199999999999995,17.913333333333334]
["Maastricht0628","Maastricht","06","28",3.6733333333333329,18.086666666666666]
["Maastricht0629","Maastricht","06","29",3.4,17.493333333333332]
["Maastricht0630","Maastricht","06","30",3.3333333333333339,17.986666666666668]
["Maastricht0701","Maastricht","07","01",3.9800000000000009,18.200000000000003]
["Maastricht0702","Maastricht","07","02",3.74,18.599999999999998]
["Maastricht0703","Maastricht","07","03",3.9199999999999995,18.539999999999996]
["Maastricht0704","Maastricht","07","04",3.78,18.506666666666668]
["Maastricht0705","Maastricht","07","05",3.6066666666666669,18.453333333333333]
["Maastricht0706","Maastricht","07","06",3.7866666666666671,18.106666666666669]
["Maastricht0707","Maastricht","07","07",4.1733333333333338,17.626666666666669]
["Maastricht0708","Maastricht","07","08",4.1000000000000005,17.333333333333332]
["Maastricht0709","Maastricht","07","09",4.1466666666666665,17.393333333333331]
["Maastricht0710","Maastricht","07","10",3.873333333333334,17.866666666666671]
["Maastricht0711","Maastricht","07","11",4.38,17.413333333333338]
["Maastricht0712","Maastricht","07","12",3.753333333333333,16.940000000000001]
["Maastricht0713","Maastricht","07","13",3.5333333333333328,17.526666666666664]
["Maastricht0714","Maastricht","07","14",4.1533333333333333,17.920000000000002]
["Maastricht0715","Maastricht","07","15",4.0666666666666664,18.920000000000002]
["Maastricht0716","Maastricht","07","16",3.7333333333333338,19.606666666666666]
["Maastricht0717","Maastricht","07","17",3.96,18.673333333333336]
["Maastricht0718","Maastricht","07","18",4.0333333333333341,19.180000000000003]
["Maastricht0719","Maastricht","07","19",3.72,19.233333333333334]
["Maastricht0720","Maastricht","07","20",3.3533333333333331,18.380000000000003]
["Maastricht0721","Maastricht","07","21",3.2333333333333334,18.573333333333334]
["Maastricht0722","Maastricht","07","22",2.9733333333333336,18.893333333333331]
["Maastricht0723","Maastricht","07","23",3.2133333333333329,18.626666666666665]
["Maastricht0724","Maastricht","07","24",3.6066666666666665,18.420000000000002]
["Maastricht0725","Maastricht","07","25",3.4266666666666663,19.006666666666668]
["Maastricht0726","Maastricht","07","26",2.9733333333333336,19.346666666666668]
["Maastricht0727","Maastricht","07","27",2.8599999999999994,20.100000000000005]
["Maastricht0728","Maastricht","07","28",2.8466666666666662,19.86]
["Maastricht0729","Maastricht","07","29",3.2399999999999998,19.340000000000007]
["Maastricht0730","Maastricht","07","30",3.566666666666666,18.48]
["Maastricht0731","Maastricht","07","31",2.8666666666666671,18.746666666666666]
["Maastricht0801","Maastricht","08","01",2.9200000000000004,19.826666666666664]
["Maastricht0802","Maastricht","08","02",3.4600000000000004,19.733333333333331]
["Maastricht0803","Maastricht","08","03",3.1,18.573333333333334]
["Maastricht0804","Maastricht","08","04",3.1066666666666665,18.84]
["Maastricht0805","Maastricht","08","05",3.2066666666666674,19.40666666666667]
["Maastricht0806","Maastricht","08","06",3.4466666666666659,19.586666666666662]
["Maastricht0807","Maastricht","08","07",3.3333333333333339,18.7]
["Maastricht0808","Maastricht","08","08",3.3133333333333335,17.899999999999999]
["Maastricht0809","Maastricht","08","09",3.2,17.826666666666664]
["Maastricht0810","Maastricht","08","10",3.64,17.54]
["Maastricht0811","Maastricht","08","11",3.4733333333333332,18.060000000000002]
["Maastricht0812","Maastricht","08","12",3.6533333333333338,18.206666666666667]
["Maastricht0813","Maastricht","08","13",3.5133333333333336,17.926666666666669]
["Maastricht0814","Maastricht","08","14",3.3533333333333331,18.013333333333335]
["Maastricht0815","Maastricht","08","15",3.5999999999999996,18.559999999999999]
["Maastricht0816","Maastricht","08","16",3.06,18.253333333333334]
["Maastricht0817","Maastricht","08","17",3.6000000000000005,18.533333333333335]
["Maastricht0818","Maastricht","08","18",3.6533333333333338,19.386666666666667]
["Maastricht0819","Maastricht","08","19",4.0266666666666664,19.220000000000002]
["Maastricht0820","Maastricht","08","20",3.6466666666666669,18.279999999999998]
["Maastricht0821","Maastricht","08","21",3.1266666666666669,17.90666666666667]
["Maastricht0822","Maastricht","08","22",2.72,17.279999999999998]
["Maastricht0823","Maastricht","08","23",3.1466666666666665,17.913333333333334]
["Maastricht0824","Maastricht","08","24",3.4200000000000004,17.673333333333336]
["Maastricht0825","Maastricht","08","25",3.3933333333333326,17.306666666666668]
["Maastricht0826","Maastricht","08","26",3.9399999999999991,17.706666666666667]
["Maastricht0827","Maastricht","08","27",3.4666666666666668,16.706666666666663]
["Maastricht0828","Maastricht","08","28",3.3666666666666658,16.213333333333331]
["Maastricht0829","Maastricht","08","29",3.4200000000000004,15.893333333333334]
["Maastricht0830","Maastricht","08","30",3.526666666666666,15.7]
["Maastricht0831","Maastricht","08","31",3.3466666666666662,16.100000000000001]
["Maastricht0901","Maastricht","09","01",3.1933333333333334,15.626666666666665]
["Maastricht0902","Maastricht","09","02",3.7399999999999998,16.346666666666668]
["Maastricht0903","Maastricht","09","03",3.96,16.54666666666667]
["Maastricht0904","Maastricht","09","04",3.3266666666666671,16.473333333333336]
["Maastricht0905","Maastricht","09","05",3.3,16.986666666666668]
["Maastricht0906","Maastricht","09","06",4,16.96]
["Maastricht0907","Maastricht","09","07",3.753333333333333,16.386666666666667]
["Maastricht0908","Maastricht","09","08",3.46,16.399999999999999]
["Maastricht0909","Maastricht","09","09",3.3,16.500000000000004]
["Maastricht0910","Maastricht","09","10",3.6066666666666669,16.566666666666666]
["Maastricht0911","Maastricht","09","11",3.5866666666666669,16.326666666666668]
["Maastricht0912","Maastricht","09","12",3.9066666666666667,15.620000000000003]
["Maastricht0913","Maastricht","09","13",3.7866666666666666,14.853333333333333]
["Maastricht0914","Maastricht","09","14",4.4399999999999995,14.859999999999998]
["Maastricht0915","Maastricht","09","15",3.6466666666666665,14.88]
["Maastricht0916","Maastricht","09","16",3.7333333333333329,14.419999999999996]
["Maastricht0917","Maastricht","09","17",3.28,13.853333333333332]
["Maastricht0918","Maastricht","09","18",3.2199999999999998,13.766666666666667]
["Maastricht0919","Maastricht","09","19",3.7866666666666675,14.113333333333335]
["Maastricht0920","Maastricht","09","20",3.8999999999999995,14.519999999999998]
["Maastricht0921","Maastricht","09","21",3.2533333333333334,14.56]
["Maastricht0922","Maastricht","09","22",3.4000000000000004,14.72]
["Maastricht0923","Maastricht","09","23",3.3333333333333335,14.026666666666666]
["Maastricht0924","Maastricht","09","24",3.3266666666666662,13.826666666666664]
["Maastricht0925","Maastricht","09","25",3.4599999999999995,13.173333333333334]
["Maastricht0926","Maastricht","09","26",3.3666666666666663,13.626666666666669]
["Maastricht0927","Maastricht","09","27",3.3066666666666666,13.593333333333335]
["Maastricht0928","Maastricht","09","28",3.4066666666666667,14.106666666666664]
["Maastricht0929","Maastricht","09","29",3.6066666666666665,13.906666666666665]
["Maastricht0930","Maastricht","09","30",3.4533333333333331,13.606666666666666]
["Maastricht1001","Maastricht","10","01",4.0799999999999992,13.913333333333334]
["Maastricht1002","Maastricht","10","02",4.22,13.746666666666666]
["Maastricht1003","Maastricht","10","03",4.1400000000000006,14.113333333333333]
["Maastricht1004","Maastricht","10","04",4.0333333333333332,13.693333333333333]
["Maastricht1005","Maastricht","10","05",4.4933333333333332,13.206666666666667]
["Maastricht1006","Maastricht","10","06",4.5066666666666659,12.993333333333332]
["Maastricht1007","Maastricht","10","07",3.6933333333333338,12.066666666666666]
["Maastricht1008","Maastricht","10","08",3.5600000000000005,11.626666666666665]
["Maastricht1009","Maastricht","10","09",3.9266666666666654,11.780000000000001]
["Maastricht1010","Maastricht","10","10",4.4466666666666663,12.06]
["Maastricht1011","Maastricht","10","11",3.9466666666666668,11.54]
["Maastricht1012","Maastricht","10","12",3.4466666666666663,11.453333333333331]
["Maastricht1013","Maastricht","10","13",3.6933333333333334,11.5]
["Maastricht1014","Maastricht","10","14",3.8733333333333331,10.753333333333332]
["Maastricht1015","Maastricht","10","15",3.9799999999999982,10.7]
["Maastricht1016","Maastricht","10","16",4.4666666666666659,10.58666666666667]
["Maastricht1017","Maastricht","10","17",4.2666666666666666,10.18]
["Maastricht1018","Maastricht","10","18",4.0199999999999996,10.606666666666667]
["Maastricht1019","Maastricht","10","19",3.8999999999999995,11.013333333333332]
["Maastricht1020","Maastricht","10","20",4.0866666666666669,10.866666666666667]
["Maastricht1021","Maastricht","10","21",4.5533333333333328,11.266666666666667]
["Maastricht1022","Maastricht","10","22",4.1800000000000006,10.879999999999999]
["Maastricht1023","Maastricht","10","23",5.1400000000000006,10.733333333333333]
["Maastricht1024","Maastricht","10","24",5.0199999999999996,10.16]
["Maastricht1025","Maastricht","10","25",5.1599999999999993,10.993333333333334]
["Maastricht1026","Maastricht","10","26",5.1933333333333325,11.020000000000001]
["Maastricht1027","Maastricht","10","27",4.7733333333333317,10.366666666666667]
["Maastricht1028","Maastricht","10","28",4.38,9.8533333333333317]
["Maastricht1029","Maastricht","10","29",4.4333333333333345,10.059999999999999]
["Maastricht1030","Maastricht","10","30",4.0999999999999988,10.16]
["Maastricht1031","Maastricht","10","31",4.18,10.080000000000002]
["Maastricht1101","Maastricht","11","01",4.5133333333333336,9.7466666666666661]
["Maastricht1102","Maastricht","11","02",4.7933333333333339,10.106666666666666]
["Maastricht1103","Maastricht","11","03",5.42,10.479999999999999]
["Maastricht1104","Maastricht","11","04",4.4266666666666667,9.6733333333333338]
["Maastricht1105","Maastricht","11","05",4.4000000000000004,8.52]
["Maastricht1106","Maastricht","11","06",4.5,8.7333333333333325]
["Maastricht1107","Maastricht","11","07",4.7,8.26]
["Maastricht1108","Maastricht","11","08",5.0600000000000005,8.1066666666666674]
["Maastricht1109","Maastricht","11","09",4.2333333333333334,7.4666666666666668]
["Maastricht1110","Maastricht","11","10",4.22,6.8933333333333326]
["Maastricht1111","Maastricht","11","11",5.2,6.9466666666666663]
["Maastricht1112","Maastricht","11","12",4.7666666666666666,7.4866666666666664]
["Maastricht1113","Maastricht","11","13",4.2866666666666662,7.7600000000000007]
["Maastricht1114","Maastricht","11","14",4.5266666666666673,7.0933333333333328]
["Maastricht1115","Maastricht","11","15",3.7266666666666666,6.133333333333332]
["Maastricht1116","Maastricht","11","16",3.2466666666666666,6.0466666666666669]
["Maastricht1117","Maastricht","11","17",4.1866666666666665,6.3266666666666662]
["Maastricht1118","Maastricht","11","18",4.246666666666667,6.7866666666666653]
["Maastricht1119","Maastricht","11","19",3.9133333333333327,6.5266666666666664]
["Maastricht1120","Maastricht","11","20",4.2399999999999993,6.5]
["Maastricht1121","Maastricht","11","21",4.4933333333333341,6.6000000000000005]
["Maastricht1122","Maastricht","11","22",4.9866666666666664,6.8933333333333326]
["Maastricht1123","Maastricht","11","23",4.5333333333333332,6.8533333333333335]
["Maastricht1124","Maastricht","11","24",4.0199999999999996,5.92]
["Maastricht1125","Maastricht","11","25",5.366666666666668,6.1133333333333333]
["Maastricht1126","Maastricht","11","26",5.006666666666665,5.6466666666666665]
["Maastricht1127","Maastricht","11","27",4.2399999999999993,5.7333333333333334]
["Maastricht1128","Maastricht","11","28",4.206666666666667,5.6666666666666661]
["Maastricht1129","Maastricht","11","29",4.6066666666666674,5.52]
["Maastricht1130","Maastricht","11","30",3.62,5.0333333333333332]
["Maastricht1201","Maastricht","12","01",4.7733333333333317,5.6266666666666669]
["Maastricht1202","Maastricht","12","02",4.5266666666666673,5.0600000000000014]
["Maastricht1203","Maastricht","12","03",4.6799999999999988,4.5866666666666678]
["Maastricht1204","Maastricht","12","04",5.1666666666666661,4.9000000000000012]
["Maastricht1205","Maastricht","12","05",5.5733333333333333,5.9599999999999991]
["Maastricht1206","Maastricht","12","06",4.9533333333333331,5.12]
["Maastricht1207","Maastricht","12","07",4.9466666666666663,4.2]
["Maastricht1208","Maastricht","12","08",5.0333333333333341,3.5533333333333332]
["Maastricht1209","Maastricht","12","09",4.78,3.1266666666666669]
["Maastricht1210","Maastricht","12","10",4.2133333333333338,2.6599999999999997]
["Maastricht1211","Maastricht","12","11",4.8333333333333321,3.1]
["Maastricht1212","Maastricht","12","12",4.5999999999999996,3.2866666666666671]
["Maastricht1213","Maastricht","12","13",5.0533333333333328,2.8933333333333335]
["Maastricht1214","Maastricht","12","14",4.9000000000000004,2.753333333333333]
["Maastricht1215","Maastricht","12","15",5.2266666666666657,3.1199999999999997]
["Maastricht1216","Maastricht","12","16",4.9933333333333341,3.36]
["Maastricht1217","Maastricht","12","17",4.2266666666666657,2.1333333333333333]
["Maastricht1218","Maastricht","12","18",4.0733333333333333,2.3066666666666662]
["Maastricht1219","Maastricht","12","19",4.1866666666666665,2.2400000000000002]
["Maastricht1220","Maastricht","12","20",4.3999999999999995,1.8466666666666667]
["Maastricht1221","Maastricht","12","21",4.6999999999999993,2.92]
["Maastricht1222","Maastricht","12","22",4.9000000000000004,3.8933333333333326]
["Maastricht1223","Maastricht","12","23",4.953333333333334,4.24]
["Maastricht1224","Maastricht","12","24",5.64,4.6999999999999993]
["Maastricht1225","Maastricht","12","25",5.3466666666666667,4.0933333333333328]
["Maastricht1226","Maastricht","12","26",4.8533333333333326,3.18]
["Maastricht1227","Maastricht","12","27",5.6,2.94]
["Maastricht1228","Maastricht","12","28",5.5933333333333328,2.9]
["Maastricht1229","Maastricht","12","29",4.9866666666666664,2.8466666666666667]
["Maastricht1230","Maastricht","12","30",5.2,3.3466666666666662]
["Maastricht1231","Maastricht","12","31",4.9133333333333322,3.4533333333333336]
["Rotterdam0101","Rotterdam","01","01",5.2733333333333343,4.5466666666666669]
["Rotterdam0102","Rotterdam","01","02",5.0666666666666664,4.16]
["Rotterdam0103","Rotterdam","01","03",5.5933333333333337,3.5600000000000005]
["Rotterdam0104","Rotterdam","01","04",5.8999999999999995,4.4400000000000004]
["Rotterdam0105","Rotterdam","01","05",5.6333333333333337,4.1800000000000006]
["Rotterdam0106","Rotterdam","01","06",4.9666666666666668,4.6066666666666674]
["Rotterdam0107","Rotterdam","01","07",5.5333333333333332,4.9000000000000004]
["Rotterdam0108","Rotterdam","01","08",5.7266666666666657,4.2399999999999993]
["Rotterdam0109","Rotterdam","01","09",5.1933333333333334,3.6266666666666665]
["Rotterdam0110","Rotterdam","01","10",4.9933333333333341,3.7866666666666671]
["Rotterdam0111","Rotterdam","01","11",5.8533333333333335,4.2533333333333339]
["Rotterdam0112","Rotterdam","01","12",5.753333333333333,3.9866666666666659]
["Rotterdam0113","Rotterdam","01","13",5.8533333333333335,4.3933333333333335]
["Rotterdam0114","Rotterdam","01","14",4.746666666666667,4.0600000000000005]
["Rotterdam0115","Rotterdam","01","15",5.12,3.56]
["Rotterdam0116","Rotterdam","01","16",5.0266666666666664,3.6]
["Rotterdam0117","Rotterdam","01","17",5.5133333333333336,4.26]
["Rotterdam0118","Rotterdam","01","18",5.6533333333333333,4.5933333333333337]
["Rotterdam0119","Rotterdam","01","19",5.7133333333333329,5.4266666666666659]
["Rotterdam0120","Rotterdam","01","20",6.5599999999999987,5.3466666666666667]
["Rotterdam0121","Rotterdam","01","21",5.7266666666666657,4.9866666666666664]
["Rotterdam0122","Rotterdam","01","22",5.2666666666666666,4.0666666666666664]
["Rotterdam0123","Rotterdam","01","23",4.8199999999999985,3.3600000000000003]
["Rotterdam0124","Rotterdam","01","24",3.98,2.8333333333333335]
["Rotterdam0125","Rotterdam","01","25",4.6400000000000006,2.3599999999999994]
["Rotterdam0126","Rotterdam","01","26",5.4933333333333341,3.0933333333333333]
["Rotterdam0127","Rotterdam","01","27",5.0999999999999996,3.6066666666666669]
["Rotterdam0128","Rotterdam","01","28",5.96,3.8733333333333335]
["Rotterdam0129","Rotterdam","01","29",5.9066666666666663,3.8266666666666671]
["Rotterdam0130","Rotterdam","01","30",4.9133333333333331,3.9266666666666672]
["Rotterdam0131","Rotterdam","01","31",6.4399999999999995,3.4933333333333336]
["Rotterdam0201","Rotterdam","02","01",6.1266666666666669,3.6199999999999992]
["Rotterdam0202","Rotterdam","02","02",5.9999999999999991,4.2666666666666666]
["Rotterdam0203","Rotterdam","02","03",4.6866666666666665,4.4599999999999991]
["Rotterdam0204","Rotterdam","02","04",6.0066666666666659,5.293333333333333]
["Rotterdam0205","Rotterdam","02","05",6.6,5.666666666666667]
["Rotterdam0206","Rotterdam","02","06",5.5133333333333336,4.9933333333333341]
["Rotterdam0207","Rotterdam","02","07",5.66,4.3066666666666658]
["Rotterdam0208","Rotterdam","02","08",5.8266666666666671,4.0466666666666669]
["Rotterdam0209","Rotterdam","02","09",5.4733333333333327,3.6400000000000006]
["Rotterdam0210","Rotterdam","02","10",5.3533333333333344,3.6600000000000006]
["Rotterdam0211","Rotterdam","02","11",5.3,4.1933333333333334]
["Rotterdam0212","Rotterdam","02","12",5.3466666666666667,4.0133333333333336]
["Rotterdam0213","Rotterdam","02","13",4.3533333333333335,3.726666666666667]
["Rotterdam0214","Rotterdam","02","14",4.5066666666666659,3.2933333333333334]
["Rotterdam0215","Rotterdam","02","15",4.9733333333333327,4.1000000000000005]
["Rotterdam0216","Rotterdam","02","16",4.34,3.7666666666666666]
["Rotterdam0217","Rotterdam","02","17",3.6066666666666665,3.4933333333333332]
["Rotterdam0218","Rotterdam","02","18",3.9333333333333327,3.5666666666666669]
["Rotterdam0219","Rotterdam","02","19",4.9466666666666672,3.7133333333333334]
["Rotterdam0220","Rotterdam","02","20",4.7733333333333317,3.4666666666666659]
["Rotterdam0221","Rotterdam","02","21",5.120000000000001,3.566666666666666]
["Rotterdam0222","Rotterdam","02","22",5.8266666666666671,4.1933333333333334]
["Rotterdam0223","Rotterdam","02","23",5.0733333333333333,4.2399999999999993]
["Rotterdam0224","Rotterdam","02","24",4.6933333333333325,5.1333333333333337]
["Rotterdam0225","Rotterdam","02","25",4.9333333333333336,5.0066666666666668]
["Rotterdam0226","Rotterdam","02","26",5.66,5.4399999999999986]
["Rotterdam0227","Rotterdam","02","27",5.52,4.8533333333333326]
["Rotterdam0228","Rotterdam","02","28",4.8133333333333335,4.9733333333333327]
["Rotterdam0229","Rotterdam","02","29",5.5250000000000004,5.4749999999999996]
["Rotterdam0301","Rotterdam","03","01",5.0733333333333333,4.84]
["Rotterdam0302","Rotterdam","03","02",4.5733333333333341,4.16]
["Rotterdam0303","Rotterdam","03","03",4.453333333333334,3.8666666666666667]
["Rotterdam0304","Rotterdam","03","04",4.1733333333333329,3.9600000000000004]
["Rotterdam0305","Rotterdam","03","05",3.9466666666666663,4.7600000000000007]
["Rotterdam0306","Rotterdam","03","06",5.42,5.28]
["Rotterdam0307","Rotterdam","03","07",5.1333333333333337,5.9266666666666659]
["Rotterdam0308","Rotterdam","03","08",5.6066666666666665,6.7866666666666662]
["Rotterdam0309","Rotterdam","03","09",5.98,6.8933333333333326]
["Rotterdam0310","Rotterdam","03","10",5.6733333333333329,6.0733333333333341]
["Rotterdam0311","Rotterdam","03","11",5.7933333333333339,6.3133333333333326]
["Rotterdam0312","Rotterdam","03","12",4.6066666666666656,5.9333333333333336]
["Rotterdam0313","Rotterdam","03","13",4.0533333333333337,6.0133333333333336]
["Rotterdam0314","Rotterdam","03","14",4.1999999999999993,6.04]
["Rotterdam0315","Rotterdam","03","15",5.0400000000000009,7.2399999999999993]
["Rotterdam0316","Rotterdam","03","16",4.7266666666666657,8.1066666666666656]
["Rotterdam0317","Rotterdam","03","17",4.793333333333333,7.2866666666666671]
["Rotterdam0318","Rotterdam","03","18",4.9800000000000004,6.7333333333333325]
["Rotterdam0319","Rotterdam","03","19",4.38,6.2133333333333347]
["Rotterdam0320","Rotterdam","03","20",4.8200000000000012,6.66]
["Rotterdam0321","Rotterdam","03","21",4.4800000000000004,6.1266666666666669]
["Rotterdam0322","Rotterdam","03","22",4.5066666666666659,6.4466666666666663]
["Rotterdam0323","Rotterdam","03","23",3.9933333333333327,6.48]
["Rotterdam0324","Rotterdam","03","24",4.0666666666666655,7.133333333333332]
["Rotterdam0325","Rotterdam","03","25",4.3066666666666666,7.2200000000000006]
["Rotterdam0326","Rotterdam","03","26",3.8466666666666662,7.0866666666666678]
["Rotterdam0327","Rotterdam","03","27",4.0200000000000005,7.0666666666666664]
["Rotterdam0328","Rotterdam","03","28",4.3666666666666663,7.5733333333333324]
["Rotterdam0329","Rotterdam","03","29",3.6266666666666665,7.84]
["Rotterdam0330","Rotterdam","03","30",4.2333333333333325,8.6400000000000023]
["Rotterdam0331","Rotterdam","03","31",4.753333333333333,8.9133333333333322]
["Rotterdam0401","Rotterdam","04","01",4.6599999999999993,9.4933333333333341]
["Rotterdam0402","Rotterdam","04","02",4.8866666666666667,10.486666666666666]
["Rotterdam0403","Rotterdam","04","03",4.5333333333333323,9.7466666666666661]
["Rotterdam0404","Rotterdam","04","04",4.919999999999999,8.44]
["Rotterdam0405","Rotterdam","04","05",5.14,7.4799999999999995]
["Rotterdam0406","Rotterdam","04","06",4.8466666666666658,8.2266666666666666]
["Rotterdam0407","Rotterdam","04","07",4.2,7.7133333333333347]
["Rotterdam0408","Rotterdam","04","08",4.206666666666667,7.0933333333333337]
["Rotterdam0409","Rotterdam","04","09",3.8133333333333335,7.5666666666666655]
["Rotterdam0410","Rotterdam","04","10",3.7,8.2799999999999994]
["Rotterdam0411","Rotterdam","04","11",3.64,8.466666666666665]
["Rotterdam0412","Rotterdam","04","12",4.0533333333333337,8.2733333333333334]
["Rotterdam0413","Rotterdam","04","13",4.0133333333333328,8.8533333333333317]
["Rotterdam0414","Rotterdam","04","14",3.7133333333333329,9.6333333333333311]
["Rotterdam0415","Rotterdam","04","15",3.9866666666666659,10.233333333333333]
["Rotterdam0416","Rotterdam","04","16",3.6333333333333333,10.026666666666667]
["Rotterdam0417","Rotterdam","04","17",4.1133333333333333,10.113333333333335]
["Rotterdam0418","Rotterdam","04","18",5.1933333333333325,9.5533333333333328]
["Rotterdam0419","Rotterdam","04","19",4.1466666666666665,9.3333333333333339]
["Rotterdam0420","Rotterdam","04","20",3.6600000000000006,10.240000000000002]
["Rotterdam0421","Rotterdam","04","21",3.1933333333333334,10.580000000000002]
["Rotterdam0422","Rotterdam","04","22",3.0866666666666664,10.786666666666667]
["Rotterdam0423","Rotterdam","04","23",2.6933333333333334,11.060000000000002]
["Rotterdam0424","Rotterdam","04","24",2.9,12.486666666666666]
["Rotterdam0425","Rotterdam","04","25",3.5666666666666673,13.360000000000001]
["Rotterdam0426","Rotterdam","04","26",4.0733333333333333,12.226666666666667]
["Rotterdam0427","Rotterdam","04","27",4.4000000000000004,12.286666666666665]
["Rotterdam0428","Rotterdam","04","28",4.3533333333333335,12.306666666666668]
["Rotterdam0429","Rotterdam","04","29",4.42,12.24]
["Rotterdam0430","Rotterdam","04","30",4.2866666666666653,12.346666666666668]
["Rotterdam0501","Rotterdam","05","01",4.633333333333332,12.42]
["Rotterdam0502","Rotterdam","05","02",4.0066666666666668,11.460000000000003]
["Rotterdam0503","Rotterdam","05","03",3.7266666666666666,11.233333333333333]
["Rotterdam0504","Rotterdam","05","04",4.1533333333333333,11.340000000000002]
["Rotterdam0505","Rotterdam","05","05",3.9466666666666663,11.833333333333336]
["Rotterdam0506","Rotterdam","05","06",4.0133333333333328,12.933333333333335]
["Rotterdam0507","Rotterdam","05","07",4.1666666666666661,13.393333333333333]
["Rotterdam0508","Rotterdam","05","08",4.3666666666666663,13.526666666666667]
["Rotterdam0509","Rotterdam","05","09",3.566666666666666,13.940000000000001]
["Rotterdam0510","Rotterdam","05","10",4.2466666666666661,14.046666666666665]
["Rotterdam0511","Rotterdam","05","11",4.8533333333333335,13.139999999999999]
["Rotterdam0512","Rotterdam","05","12",4.3533333333333335,12.633333333333336]
["Rotterdam0513","Rotterdam","05","13",4.0200000000000005,13.346666666666666]
["Rotterdam0514","Rotterdam","05","14",4.2133333333333329,12.453333333333335]
["Rotterdam0515","Rotterdam","05","15",3.5666666666666673,12.659999999999998]
["Rotterdam0516","Rotterdam","05","16",3.7866666666666666,12.666666666666666]
["Rotterdam0517","Rotterdam","05","17",4.1466666666666656,12.486666666666666]
["Rotterdam0518","Rotterdam","05","18",4.4866666666666672,12.92]
["Rotterdam0519","Rotterdam","05","19",4.3133333333333326,12.986666666666666]
["Rotterdam0520","Rotterdam","05","20",3.7733333333333334,13.660000000000002]
["Rotterdam0521","Rotterdam","05","21",3.6000000000000005,14.02]
["Rotterdam0522","Rotterdam","05","22",4.5,13.933333333333334]
["Rotterdam0523","Rotterdam","05","23",4.0866666666666669,14.34]
["Rotterdam0524","Rotterdam","05","24",4.1533333333333333,14.373333333333333]
["Rotterdam0525","Rotterdam","05","25",4.26,14.613333333333333]
["Rotterdam0526","Rotterdam","05","26",4.5999999999999996,14.046666666666669]
["Rotterdam0527","Rotterdam","05","27",4.0533333333333328,14.42]
["Rotterdam0528","Rotterdam","05","28",4.46,14.646666666666663]
["Rotterdam0529","Rotterdam","05","29",4.26,13.733333333333336]
["Rotterdam0530","Rotterdam","05","30",3.4599999999999995,14.206666666666667]
["Rotterdam0531","Rotterdam","05","31",3.48,13.600000000000001]
["Rotterdam0601","Rotterdam","06","01",3.0866666666666669,14.326666666666666]
["Rotterdam0602","Rotterdam","06","02",3.4066666666666663,15.066666666666666]
["Rotterdam0603","Rotterdam","06","03",3.5866666666666664,14.913333333333332]
["Rotterdam0604","Rotterdam","06","04",4.1066666666666665,15.153333333333332]
["Rotterdam0605","Rotterdam","06","05",3.3400000000000003,14.679999999999998]
["Rotterdam0606","Rotterdam","06","06",3.4999999999999991,15.08]
["Rotterdam0607","Rotterdam","06","07",3.4533333333333331,15.52]
["Rotterdam0608","Rotterdam","06","08",3.6600000000000006,16.240000000000002]
["Rotterdam0609","Rotterdam","06","09",3.52,16.233333333333334]
["Rotterdam0610","Rotterdam","06","10",3.1933333333333334,15.78]
["Rotterdam0611","Rotterdam","06","11",3.7600000000000002,15.360000000000003]
["Rotterdam0612","Rotterdam","06","12",3.6933333333333334,15.266666666666667]
["Rotterdam0613","Rotterdam","06","13",3.6600000000000006,15.233333333333333]
["Rotterdam0614","Rotterdam","06","14",3.5266666666666664,16.079999999999998]
["Rotterdam0615","Rotterdam","06","15",4,15.613333333333333]
["Rotterdam0616","Rotterdam","06","16",3.9,15.473333333333333]
["Rotterdam0617","Rotterdam","06","17",3.86,17.079999999999998]
["Rotterdam0618","Rotterdam","06","18",3.8466666666666662,17.166666666666668]
["Rotterdam0619","Rotterdam","06","19",4.1599999999999993,17.086666666666666]
["Rotterdam0620","Rotterdam","06","20",3.7933333333333339,16.920000000000002]
["Rotterdam0621","Rotterdam","06","21",4.1199999999999992,16.113333333333333]
["Rotterdam0622","Rotterdam","06","22",4.833333333333333,16.306666666666661]
["Rotterdam0623","Rotterdam","06","23",4.6933333333333325,16.553333333333335]
["Rotterdam0624","Rotterdam","06","24",3.9066666666666667,16.453333333333333]
["Rotterdam0625","Rotterdam","06","25",3.6133333333333328,16.113333333333333]
["Rotterdam0626","Rotterdam","06","26",3.4733333333333332,16.866666666666667]
["Rotterdam0627","Rotterdam","06","27",3.9133333333333336,17.339999999999996]
["Rotterdam0628","Rotterdam","06","28",3.9133333333333331,17.459999999999997]
["Rotterdam0629","Rotterdam","06","29",3.74,16.866666666666671]
["Rotterdam0630","Rotterdam","06","30",3.5933333333333333,17.406666666666663]
["Rotterdam0701","Rotterdam","07","01",4.1466666666666665,17.233333333333334]
["Rotterdam0702","Rotterdam","07","02",3.9533333333333331,18.533333333333335]
["Rotterdam0703","Rotterdam","07","03",4.1466666666666665,18.079999999999998]
["Rotterdam0704","Rotterdam","07","04",3.8333333333333326,18.439999999999998]
["Rotterdam0705","Rotterdam","07","05",3.566666666666666,18.240000000000002]
["Rotterdam0706","Rotterdam","07","06",3.9066666666666667,17.626666666666669]
["Rotterdam0707","Rotterdam","07","07",4.3066666666666666,17.339999999999996]
["Rotterdam0708","Rotterdam","07","08",3.8933333333333326,17.126666666666665]
["Rotterdam0709","Rotterdam","07","09",4.46,17.259999999999998]
["Rotterdam0710","Rotterdam","07","10",4.0666666666666664,17.786666666666669]
["Rotterdam0711","Rotterdam","07","11",4.5199999999999996,17.066666666666666]
["Rotterdam0712","Rotterdam","07","12",3.9266666666666667,16.54]
["Rotterdam0713","Rotterdam","07","13",3.6,17.086666666666666]
["Rotterdam0714","Rotterdam","07","14",4.2266666666666657,17.446666666666669]
["Rotterdam0715","Rotterdam","07","15",3.9266666666666663,18.246666666666666]
["Rotterdam0716","Rotterdam","07","16",3.48,18.393333333333334]
["Rotterdam0717","Rotterdam","07","17",4.0999999999999996,18.186666666666667]
["Rotterdam0718","Rotterdam","07","18",4.546666666666666,18.326666666666664]
["Rotterdam0719","Rotterdam","07","19",3.9733333333333332,19.033333333333335]
["Rotterdam0720","Rotterdam","07","20",3.3733333333333331,18.013333333333332]
["Rotterdam0721","Rotterdam","07","21",3.586666666666666,17.933333333333334]
["Rotterdam0722","Rotterdam","07","22",3.0533333333333332,18.240000000000002]
["Rotterdam0723","Rotterdam","07","23",3.526666666666666,18.559999999999999]
["Rotterdam0724","Rotterdam","07","24",3.8,18.306666666666668]
["Rotterdam0725","Rotterdam","07","25",3.333333333333333,18.506666666666668]
["Rotterdam0726","Rotterdam","07","26",3.0066666666666668,19.060000000000002]
["Rotterdam0727","Rotterdam","07","27",2.8,19.233333333333334]
["Rotterdam0728","Rotterdam","07","28",2.98,19.453333333333333]
["Rotterdam0729","Rotterdam","07","29",3.3400000000000003,19.32]
["Rotterdam0730","Rotterdam","07","30",3.7333333333333334,18.413333333333338]
["Rotterdam0731","Rotterdam","07","31",3.2666666666666666,18.346666666666668]
["Rotterdam0801","Rotterdam","08","01",3.1133333333333328,19.073333333333334]
["Rotterdam0802","Rotterdam","08","02",3.4266666666666672,19.04]
["Rotterdam0803","Rotterdam","08","03",3.5466666666666664,18.246666666666666]
["Rotterdam0804","Rotterdam","08","04",3.6733333333333333,18.719999999999995]
["Rotterdam0805","Rotterdam","08","05",3.0733333333333333,19.060000000000002]
["Rotterdam0806","Rotterdam","08","06",3.4466666666666668,19.12]
["Rotterdam0807","Rotterdam","08","07",3.3866666666666672,18.199999999999996]
["Rotterdam0808","Rotterdam","08","08",3.7066666666666661,17.566666666666663]
["Rotterdam0809","Rotterdam","08","09",3.5466666666666669,17.613333333333333]
["Rotterdam0810","Rotterdam","08","10",3.98,17.566666666666666]
["Rotterdam0811","Rotterdam","08","11",3.6799999999999997,17.773333333333333]
["Rotterdam0812","Rotterdam","08","12",3.9533333333333331,17.540000000000003]
["Rotterdam0813","Rotterdam","08","13",4.1399999999999997,17.653333333333332]
["Rotterdam0814","Rotterdam","08","14",3.48,18.16]
["Rotterdam0815","Rotterdam","08","15",3.8133333333333335,18.546666666666667]
["Rotterdam0816","Rotterdam","08","16",3.5733333333333333,18.36]
["Rotterdam0817","Rotterdam","08","17",3.9933333333333327,18.413333333333334]
["Rotterdam0818","Rotterdam","08","18",4.04,19.186666666666664]
["Rotterdam0819","Rotterdam","08","19",4.1666666666666661,18.686666666666667]
["Rotterdam0820","Rotterdam","08","20",3.6599999999999997,17.913333333333338]
["Rotterdam0821","Rotterdam","08","21",3.5933333333333337,17.43333333333333]
["Rotterdam0822","Rotterdam","08","22",3.2800000000000002,17.266666666666666]
["Rotterdam0823","Rotterdam","08","23",3.3,17.706666666666667]
["Rotterdam0824","Rotterdam","08","24",3.4133333333333336,17.313333333333333]
["Rotterdam0825","Rotterdam","08","25",3.64,17.34]
["Rotterdam0826","Rotterdam","08","26",4.0933333333333328,17.386666666666667]
["Rotterdam0827","Rotterdam","08","27",3.5066666666666664,16.653333333333332]
["Rotterdam0828","Rotterdam","08","28",3.5600000000000005,16.146666666666668]
["Rotterdam0829","Rotterdam","08","29",3.7933333333333334,15.966666666666667]
["Rotterdam0830","Rotterdam","08","30",3.7199999999999998,16]
["Rotterdam0831","Rotterdam","08","31",3.4866666666666668,16.46]
["Rotterdam0901","Rotterdam","09","01",3.3333333333333335,15.833333333333327]
["Rotterdam0902","Rotterdam","09","02",3.7999999999999994,16.419999999999998]
["Rotterdam0903","Rotterdam","09","03",3.9000000000000004,16.720000000000002]
["Rotterdam0904","Rotterdam","09","04",3.32,16.14]
["Rotterdam0905","Rotterdam","09","05",3.58,17.113333333333337]
["Rotterdam0906","Rotterdam","09","06",4.2733333333333343,17.240000000000002]
["Rotterdam0907","Rotterdam","09","07",4.3933333333333326,16.426666666666666]
["Rotterdam0908","Rotterdam","09","08",3.4533333333333336,16.213333333333335]
["Rotterdam0909","Rotterdam","09","09",3.4333333333333327,16.386666666666667]
["Rotterdam0910","Rotterdam","09","10",3.7133333333333329,16.400000000000002]
["Rotterdam0911","Rotterdam","09","11",3.7800000000000002,16.8]
["Rotterdam0912","Rotterdam","09","12",4.04,15.919999999999998]
["Rotterdam0913","Rotterdam","09","13",3.6533333333333338,15.213333333333333]
["Rotterdam0914","Rotterdam","09","14",4.4066666666666663,15.293333333333333]
["Rotterdam0915","Rotterdam","09","15",3.5266666666666668,14.879999999999999]
["Rotterdam0916","Rotterdam","09","16",3.4533333333333336,14.600000000000001]
["Rotterdam0917","Rotterdam","09","17",3.2466666666666666,14.280000000000003]
["Rotterdam0918","Rotterdam","09","18",3.2133333333333325,14.153333333333336]
["Rotterdam0919","Rotterdam","09","19",3.6933333333333329,14.233333333333333]
["Rotterdam0920","Rotterdam","09","20",3.88,14.906666666666666]
["Rotterdam0921","Rotterdam","09","21",3.5333333333333332,15.026666666666667]
["Rotterdam0922","Rotterdam","09","22",3.5466666666666664,15.039999999999997]
["Rotterdam0923","Rotterdam","09","23",3.4266666666666667,14.533333333333333]
["Rotterdam0924","Rotterdam","09","24",3.6066666666666669,13.986666666666666]
["Rotterdam0925","Rotterdam","09","25",3.333333333333333,13.67333333333333]
["Rotterdam0926","Rotterdam","09","26",3.1799999999999997,13.759999999999998]
["Rotterdam0927","Rotterdam","09","27",3.0200000000000005,13.866666666666667]
["Rotterdam0928","Rotterdam","09","28",3.6799999999999997,14.56]
["Rotterdam0929","Rotterdam","09","29",3.4999999999999996,14.3]
["Rotterdam0930","Rotterdam","09","30",3.6599999999999997,13.959999999999999]
["Rotterdam1001","Rotterdam","10","01",4.2466666666666661,14.113333333333333]
["Rotterdam1002","Rotterdam","10","02",4.2399999999999993,13.926666666666668]
["Rotterdam1003","Rotterdam","10","03",4.453333333333334,14.359999999999998]
["Rotterdam1004","Rotterdam","10","04",4.4599999999999991,13.66]
["Rotterdam1005","Rotterdam","10","05",4.3333333333333339,13.366666666666667]
["Rotterdam1006","Rotterdam","10","06",4.4666666666666668,12.886666666666667]
["Rotterdam1007","Rotterdam","10","07",4.3533333333333335,12.193333333333335]
["Rotterdam1008","Rotterdam","10","08",3.9533333333333327,12.126666666666665]
["Rotterdam1009","Rotterdam","10","09",4.0599999999999996,12.126666666666665]
["Rotterdam1010","Rotterdam","10","10",4.8066666666666666,12.573333333333331]
["Rotterdam1011","Rotterdam","10","11",4.5266666666666673,11.860000000000001]
["Rotterdam1012","Rotterdam","10","12",3.7999999999999994,11.886666666666665]
["Rotterdam1013","Rotterdam","10","13",3.6533333333333333,11.966666666666667]
["Rotterdam1014","Rotterdam","10","14",3.6066666666666669,11.259999999999998]
["Rotterdam1015","Rotterdam","10","15",3.8666666666666667,11.000000000000002]
["Rotterdam1016","Rotterdam","10","16",4.753333333333333,11.086666666666668]
["Rotterdam1017","Rotterdam","10","17",4.0066666666666668,10.686666666666667]
["Rotterdam1018","Rotterdam","10","18",4.18,11.133333333333333]
["Rotterdam1019","Rotterdam","10","19",3.913333333333334,11.533333333333333]
["Rotterdam1020","Rotterdam","10","20",4.379999999999999,11.286666666666667]
["Rotterdam1021","Rotterdam","10","21",5.1733333333333329,11.626666666666667]
["Rotterdam1022","Rotterdam","10","22",4.84,11.68]
["Rotterdam1023","Rotterdam","10","23",5.2933333333333321,11.246666666666668]
["Rotterdam1024","Rotterdam","10","24",5.1266666666666669,10.833333333333332]
["Rotterdam1025","Rotterdam","10","25",5.5866666666666678,11.446666666666665]
["Rotterdam1026","Rotterdam","10","26",5.366666666666668,11.353333333333333]
["Rotterdam1027","Rotterdam","10","27",5.3866666666666658,10.660000000000002]
["Rotterdam1028","Rotterdam","10","28",4.9666666666666668,10.759999999999998]
["Rotterdam1029","Rotterdam","10","29",4.5600000000000005,10.733333333333331]
["Rotterdam1030","Rotterdam","10","30",4.5,10.613333333333335]
["Rotterdam1031","Rotterdam","10","31",4.8066666666666666,10.640000000000002]
["Rotterdam1101","Rotterdam","11","01",4.9466666666666672,10.359999999999998]
["Rotterdam1102","Rotterdam","11","02",4.9000000000000004,10.473333333333331]
["Rotterdam1103","Rotterdam","11","03",5.3933333333333344,10.7]
["Rotterdam1104","Rotterdam","11","04",4.5466666666666669,9.9400000000000013]
["Rotterdam1105","Rotterdam","11","05",4.3666666666666663,9.5266666666666655]
["Rotterdam1106","Rotterdam","11","06",4.5866666666666678,9.6933333333333334]
["Rotterdam1107","Rotterdam","11","07",4.7733333333333343,8.9666666666666668]
["Rotterdam1108","Rotterdam","11","08",5.5533333333333328,8.7533333333333321]
["Rotterdam1109","Rotterdam","11","09",4.5666666666666664,7.7399999999999993]
["Rotterdam1110","Rotterdam","11","10",4.5333333333333323,8.1733333333333338]
["Rotterdam1111","Rotterdam","11","11",5.6733333333333338,8.1866666666666674]
["Rotterdam1112","Rotterdam","11","12",5.1466666666666656,8.4266666666666659]
["Rotterdam1113","Rotterdam","11","13",4.2666666666666666,8.3933333333333326]
["Rotterdam1114","Rotterdam","11","14",4.5600000000000005,7.98]
["Rotterdam1115","Rotterdam","11","15",3.6,6.9666666666666677]
["Rotterdam1116","Rotterdam","11","16",3.5133333333333336,7.1999999999999993]
["Rotterdam1117","Rotterdam","11","17",4.1866666666666665,7.5733333333333341]
["Rotterdam1118","Rotterdam","11","18",4.3133333333333335,7.3733333333333348]
["Rotterdam1119","Rotterdam","11","19",4.0466666666666669,7.0133333333333336]
["Rotterdam1120","Rotterdam","11","20",4.6133333333333324,7.0933333333333337]
["Rotterdam1121","Rotterdam","11","21",5.0666666666666664,6.9666666666666677]
["Rotterdam1122","Rotterdam","11","22",5.2533333333333339,7.5133333333333328]
["Rotterdam1123","Rotterdam","11","23",3.9333333333333331,7.3400000000000007]
["Rotterdam1124","Rotterdam","11","24",4.086666666666666,6.5666666666666655]
["Rotterdam1125","Rotterdam","11","25",5.4799999999999995,6.76]
["Rotterdam1126","Rotterdam","11","26",4.72,6.5399999999999983]
["Rotterdam1127","Rotterdam","11","27",4.1933333333333325,6.4733333333333336]
["Rotterdam1128","Rotterdam","11","28",4.3933333333333326,6.4133333333333322]
["Rotterdam1129","Rotterdam","11","29",4.6399999999999997,6.1799999999999988]
["Rotterdam1130","Rotterdam","11","30",4.08,5.7333333333333334]
["Rotterdam1201","Rotterdam","12","01",5.126666666666666,6.0000000000000009]
["Rotterdam1202","Rotterdam","12","02",4.3266666666666671,5.14]
["Rotterdam1203","Rotterdam","12","03",4.5666666666666664,5.0199999999999996]
["Rotterdam1204","Rotterdam","12","04",5.52,5.753333333333333]
["Rotterdam1205","Rotterdam","12","05",5.54,6.72]
["Rotterdam1206","Rotterdam","12","06",5.1066666666666665,6.126666666666666]
["Rotterdam1207","Rotterdam","12","07",5.3066666666666675,4.8933333333333326]
["Rotterdam1208","Rotterdam","12","08",4.8266666666666671,4.34]
["Rotterdam1209","Rotterdam","12","09",4.92,3.8466666666666658]
["Rotterdam1210","Rotterdam","12","10",4.5666666666666664,3.68]
["Rotterdam1211","Rotterdam","12","11",5.0400000000000009,4.5400000000000009]
["Rotterdam1212","Rotterdam","12","12",4.9200000000000008,4.4866666666666672]
["Rotterdam1213","Rotterdam","12","13",5.5666666666666655,3.8733333333333335]
["Rotterdam1214","Rotterdam","12","14",5.0999999999999996,3.3933333333333331]
["Rotterdam1215","Rotterdam","12","15",5.4999999999999991,4.1266666666666669]
["Rotterdam1216","Rotterdam","12","16",4.8733333333333331,3.9066666666666667]
["Rotterdam1217","Rotterdam","12","17",4.24,3.4]
["Rotterdam1218","Rotterdam","12","18",3.6399999999999997,3.0133333333333336]
["Rotterdam1219","Rotterdam","12","19",4.2,2.746666666666667]
["Rotterdam1220","Rotterdam","12","20",4.7133333333333329,2.8533333333333335]
["Rotterdam1221","Rotterdam","12","21",4.7733333333333325,3.6533333333333333]
["Rotterdam1222","Rotterdam","12","22",4.9133333333333322,4.5933333333333337]
["Rotterdam1223","Rotterdam","12","23",5.6,5.04]
["Rotterdam1224","Rotterdam","12","24",5.9666666666666668,5.5933333333333346]
["Rotterdam1225","Rotterdam","12","25",5.2666666666666666,5.133333333333332]
["Rotterdam1226","Rotterdam","12","26",4.84,3.8933333333333331]
["Rotterdam1227","Rotterdam","12","27",5.706666666666667,3.5333333333333328]
["Rotterdam1228","Rotterdam","12","28",5.7599999999999989,3.9066666666666658]
["Rotterdam1229","Rotterdam","12","29",5,3.8666666666666658]
["Rotterdam1230","Rotterdam","12","30",5.38,3.6533333333333329]
["Rotterdam1231","Rotterdam","12","31",5.0400000000000009,4.1133333333333333]
["Twenthe0101","Twenthe","01","01",4.04,3.12]
["Twenthe0102","Twenthe","01","02",3.8600000000000003,3.12]
["Twenthe0103","Twenthe","01","03",4.333333333333333,2.4733333333333336]
["Twenthe0104","Twenthe","01","04",4.6800000000000006,2.8933333333333335]
["Twenthe0105","Twenthe","01","05",4.293333333333333,2.8266666666666662]
["Twenthe0106","Twenthe","01","06",3.9333333333333327,3.3400000000000007]
["Twenthe0107","Twenthe","01","07",4.0999999999999996,3.8133333333333335]
["Twenthe0108","Twenthe","01","08",4.4333333333333336,3.6866666666666665]
["Twenthe0109","Twenthe","01","09",4.0333333333333332,2.3400000000000003]
["Twenthe0110","Twenthe","01","10",3.8266666666666662,2.2800000000000002]
["Twenthe0111","Twenthe","01","11",4.4733333333333336,3.2133333333333329]
["Twenthe0112","Twenthe","01","12",4.453333333333334,3.14]
["Twenthe0113","Twenthe","01","13",4.3733333333333331,3.4799999999999995]
["Twenthe0114","Twenthe","01","14",3.4399999999999995,2.933333333333334]
["Twenthe0115","Twenthe","01","15",3.6733333333333333,2.2066666666666666]
["Twenthe0116","Twenthe","01","16",3.8133333333333339,2.6066666666666665]
["Twenthe0117","Twenthe","01","17",4.5533333333333337,3.5799999999999996]
["Twenthe0118","Twenthe","01","18",4.62,3.8400000000000007]
["Twenthe0119","Twenthe","01","19",4.38,4.22]
["Twenthe0120","Twenthe","01","20",4.9266666666666667,4.2133333333333338]
["Twenthe0121","Twenthe","01","21",4.2866666666666662,3.3933333333333335]
["Twenthe0122","Twenthe","01","22",3.92,2.4133333333333331]
["Twenthe0123","Twenthe","01","23",3.6133333333333342,1.4999999999999998]
["Twenthe0124","Twenthe","01","24",3.1733333333333329,1.1266666666666671]
["Twenthe0125","Twenthe","01","25",3.58,1.0266666666666666]
["Twenthe0126","Twenthe","01","26",4.18,1.3999999999999995]
["Twenthe0127","Twenthe","01","27",4.0199999999999996,2.3266666666666667]
["Twenthe0128","Twenthe","01","28",4.5,2.4466666666666668]
["Twenthe0129","Twenthe","01","29",4.293333333333333,2.2599999999999998]
["Twenthe0130","Twenthe","01","30",3.9533333333333327,2.72]
["Twenthe0131","Twenthe","01","31",4.9266666666666659,2.2199999999999998]
["Twenthe0201","Twenthe","02","01",4.66,2.46]
["Twenthe0202","Twenthe","02","02",4.6666666666666661,3.0333333333333337]
["Twenthe0203","Twenthe","02","03",3.6333333333333329,3.2200000000000006]
["Twenthe0204","Twenthe","02","04",4.3066666666666675,3.9333333333333331]
["Twenthe0205","Twenthe","02","05",4.6133333333333342,4.5600000000000005]
["Twenthe0206","Twenthe","02","06",4.0733333333333333,4.3133333333333326]
["Twenthe0207","Twenthe","02","07",4.4266666666666659,3.3733333333333335]
["Twenthe0208","Twenthe","02","08",4.42,3.1933333333333325]
["Twenthe0209","Twenthe","02","09",4.0200000000000005,2.5133333333333336]
["Twenthe0210","Twenthe","02","10",3.9866666666666668,2.3599999999999994]
["Twenthe0211","Twenthe","02","11",3.8199999999999994,3.1]
["Twenthe0212","Twenthe","02","12",4.3066666666666666,2.94]
["Twenthe0213","Twenthe","02","13",3.4133333333333336,2.8533333333333331]
["Twenthe0214","Twenthe","02","14",3.0333333333333328,2.3066666666666671]
["Twenthe0215","Twenthe","02","15",3.5733333333333328,2.76]
["Twenthe0216","Twenthe","02","16",3.3266666666666667,2.5733333333333333]
["Twenthe0217","Twenthe","02","17",2.8400000000000003,1.8866666666666665]
["Twenthe0218","Twenthe","02","18",3.1199999999999997,2.5533333333333332]
["Twenthe0219","Twenthe","02","19",3.82,2.6533333333333333]
["Twenthe0220","Twenthe","02","20",3.9399999999999995,2.5266666666666668]
["Twenthe0221","Twenthe","02","21",4.04,2.62]
["Twenthe0222","Twenthe","02","22",4.7,3.24]
["Twenthe0223","Twenthe","02","23",3.8733333333333331,3.253333333333333]
["Twenthe0224","Twenthe","02","24",3.6733333333333333,3.92]
["Twenthe0225","Twenthe","02","25",3.7133333333333325,3.9266666666666667]
["Twenthe0226","Twenthe","02","26",4.2733333333333343,4.6133333333333333]
["Twenthe0227","Twenthe","02","27",4.0866666666666669,3.9]
["Twenthe0228","Twenthe","02","28",3.6866666666666661,4.5733333333333333]
["Twenthe0229","Twenthe","02","29",4.0750000000000002,5.3]
["Twenthe0301","Twenthe","03","01",4.26,4.04]
["Twenthe0302","Twenthe","03","02",4.0666666666666664,3.64]
["Twenthe0303","Twenthe","03","03",3.4466666666666659,2.813333333333333]
["Twenthe0304","Twenthe","03","04",3.1133333333333328,2.7266666666666666]
["Twenthe0305","Twenthe","03","05",3.2933333333333334,3.753333333333333]
["Twenthe0306","Twenthe","03","06",4.1133333333333333,4.08]
["Twenthe0307","Twenthe","03","07",3.9866666666666659,5]
["Twenthe0308","Twenthe","03","08",4.0599999999999996,5.7066666666666661]
["Twenthe0309","Twenthe","03","09",4.5866666666666669,5.9933333333333332]
["Twenthe0310","Twenthe","03","10",4.3866666666666676,5.4866666666666664]
["Twenthe0311","Twenthe","03","11",4.7266666666666675,5.6800000000000006]
["Twenthe0312","Twenthe","03","12",3.78,5.38]
["Twenthe0313","Twenthe","03","13",3.3466666666666667,5.1133333333333333]
["Twenthe0314","Twenthe","03","14",3.7,5.0866666666666651]
["Twenthe0315","Twenthe","03","15",3.9533333333333336,5.4933333333333341]
["Twenthe0316","Twenthe","03","16",3.773333333333333,7.0866666666666651]
["Twenthe0317","Twenthe","03","17",4.0199999999999996,6.96]
["Twenthe0318","Twenthe","03","18",3.8199999999999994,6.3333333333333321]
["Twenthe0319","Twenthe","03","19",3.8399999999999994,5.2266666666666657]
["Twenthe0320","Twenthe","03","20",3.6199999999999997,5.6533333333333342]
["Twenthe0321","Twenthe","03","21",3.3533333333333326,5.3200000000000021]
["Twenthe0322","Twenthe","03","22",3.46,5.3133333333333326]
["Twenthe0323","Twenthe","03","23",3.3866666666666663,5.4733333333333327]
["Twenthe0324","Twenthe","03","24",3.333333333333333,6.253333333333333]
["Twenthe0325","Twenthe","03","25",3.473333333333334,6.3266666666666671]
["Twenthe0326","Twenthe","03","26",3.1733333333333325,6.1066666666666682]
["Twenthe0327","Twenthe","03","27",3.5933333333333328,6.6866666666666674]
["Twenthe0328","Twenthe","03","28",3.6400000000000006,7.080000000000001]
["Twenthe0329","Twenthe","03","29",3.273333333333333,7.546666666666666]
["Twenthe0330","Twenthe","03","30",3.3,8.06]
["Twenthe0331","Twenthe","03","31",3.8599999999999994,8.3933333333333326]
["Twenthe0401","Twenthe","04","01",3.773333333333333,8.9533333333333349]
["Twenthe0402","Twenthe","04","02",3.9200000000000004,10.453333333333335]
["Twenthe0403","Twenthe","04","03",3.76,9.9333333333333318]
["Twenthe0404","Twenthe","04","04",3.9000000000000004,8.4866666666666664]
["Twenthe0405","Twenthe","04","05",4.18,7.08]
["Twenthe0406","Twenthe","04","06",3.7666666666666666,7.7133333333333338]
["Twenthe0407","Twenthe","04","07",3.36,7.6866666666666665]
["Twenthe0408","Twenthe","04","08",3.4533333333333336,6.4800000000000013]
["Twenthe0409","Twenthe","04","09",3.3666666666666663,7.2999999999999989]
["Twenthe0410","Twenthe","04","10",2.9599999999999995,7.4666666666666668]
["Twenthe0411","Twenthe","04","11",2.833333333333333,8.1266666666666669]
["Twenthe0412","Twenthe","04","12",3.3466666666666658,8.26]
["Twenthe0413","Twenthe","04","13",3.6066666666666669,8.6533333333333342]
["Twenthe0414","Twenthe","04","14",3.1933333333333338,9.2200000000000024]
["Twenthe0415","Twenthe","04","15",3.2266666666666666,10.173333333333336]
["Twenthe0416","Twenthe","04","16",2.9133333333333336,10.033333333333333]
["Twenthe0417","Twenthe","04","17",3.4466666666666668,10.266666666666667]
["Twenthe0418","Twenthe","04","18",3.9733333333333332,9.7199999999999989]
["Twenthe0419","Twenthe","04","19",3.4999999999999996,9.1733333333333338]
["Twenthe0420","Twenthe","04","20",2.9533333333333331,9.4533333333333349]
["Twenthe0421","Twenthe","04","21",2.8600000000000003,10.639999999999999]
["Twenthe0422","Twenthe","04","22",2.7266666666666661,10.84]
["Twenthe0423","Twenthe","04","23",2.4866666666666668,11.526666666666667]
["Twenthe0424","Twenthe","04","24",2.6933333333333338,12.773333333333332]
["Twenthe0425","Twenthe","04","25",3.0200000000000005,13.966666666666669]
["Twenthe0426","Twenthe","04","26",3.2133333333333334,12.813333333333333]
["Twenthe0427","Twenthe","04","27",3.5333333333333341,12.24]
["Twenthe0428","Twenthe","04","28",3.06,12.54]
["Twenthe0429","Twenthe","04","29",3.5533333333333332,12.353333333333333]
["Twenthe0430","Twenthe","04","30",3.186666666666667,12.520000000000001]
["Twenthe0501","Twenthe","05","01",3.6333333333333329,12.300000000000002]
["Twenthe0502","Twenthe","05","02",3.26,12.146666666666668]
["Twenthe0503","Twenthe","05","03",2.9266666666666667,11.713333333333335]
["Twenthe0504","Twenthe","05","04",3.2666666666666662,11.466666666666665]
["Twenthe0505","Twenthe","05","05",3.3199999999999994,11.773333333333333]
["Twenthe0506","Twenthe","05","06",3.3466666666666658,12.466666666666665]
["Twenthe0507","Twenthe","05","07",3.2133333333333334,12.593333333333334]
["Twenthe0508","Twenthe","05","08",3.56,13.56]
["Twenthe0509","Twenthe","05","09",3.1933333333333334,14.08]
["Twenthe0510","Twenthe","05","10",3.3533333333333335,14.313333333333333]
["Twenthe0511","Twenthe","05","11",3.9333333333333327,13.426666666666668]
["Twenthe0512","Twenthe","05","12",3.5466666666666669,12.32]
["Twenthe0513","Twenthe","05","13",3.0399999999999991,12.993333333333336]
["Twenthe0514","Twenthe","05","14",3.4333333333333331,12.639999999999997]
["Twenthe0515","Twenthe","05","15",2.8733333333333335,12.373333333333331]
["Twenthe0516","Twenthe","05","16",3.3399999999999994,12.733333333333333]
["Twenthe0517","Twenthe","05","17",2.9,12.313333333333334]
["Twenthe0518","Twenthe","05","18",3.313333333333333,12.620000000000001]
["Twenthe0519","Twenthe","05","19",3.3066666666666666,13.013333333333332]
["Twenthe0520","Twenthe","05","20",2.9999999999999996,14.039999999999997]
["Twenthe0521","Twenthe","05","21",2.9933333333333327,14.32666666666667]
["Twenthe0522","Twenthe","05","22",3.4133333333333336,14.166666666666666]
["Twenthe0523","Twenthe","05","23",2.9466666666666668,13.9]
["Twenthe0524","Twenthe","05","24",3.5200000000000005,14.506666666666666]
["Twenthe0525","Twenthe","05","25",3.3066666666666662,14.093333333333334]
["Twenthe0526","Twenthe","05","26",3.54,14.093333333333332]
["Twenthe0527","Twenthe","05","27",3.2933333333333339,14.426666666666669]
["Twenthe0528","Twenthe","05","28",3.3933333333333331,14.746666666666668]
["Twenthe0529","Twenthe","05","29",3.5333333333333332,13.96666666666667]
["Twenthe0530","Twenthe","05","30",2.6533333333333333,14.486666666666666]
["Twenthe0531","Twenthe","05","31",3.1666666666666665,13.819999999999999]
["Twenthe0601","Twenthe","06","01",2.7666666666666671,14.213333333333333]
["Twenthe0602","Twenthe","06","02",3.086666666666666,15.206666666666665]
["Twenthe0603","Twenthe","06","03",3.0999999999999996,15.233333333333336]
["Twenthe0604","Twenthe","06","04",3.1733333333333333,15.326666666666666]
["Twenthe0605","Twenthe","06","05",2.8466666666666662,14.953333333333337]
["Twenthe0606","Twenthe","06","06",2.54,15.44]
["Twenthe0607","Twenthe","06","07",2.8866666666666672,16.146666666666665]
["Twenthe0608","Twenthe","06","08",2.7733333333333334,16.7]
["Twenthe0609","Twenthe","06","09",2.8733333333333335,16.779999999999998]
["Twenthe0610","Twenthe","06","10",2.5466666666666664,16.586666666666666]
["Twenthe0611","Twenthe","06","11",3.08,15.5]
["Twenthe0612","Twenthe","06","12",2.9266666666666667,15.113333333333333]
["Twenthe0613","Twenthe","06","13",2.813333333333333,15.093333333333334]
["Twenthe0614","Twenthe","06","14",2.72,15.606666666666667]
["Twenthe0615","Twenthe","06","15",3.0999999999999996,15.726666666666668]
["Twenthe0616","Twenthe","06","16",3.1,15.006666666666662]
["Twenthe0617","Twenthe","06","17",3.0266666666666664,16.56666666666667]
["Twenthe0618","Twenthe","06","18",3.0999999999999996,17.139999999999997]
["Twenthe0619","Twenthe","06","19",3.2600000000000002,16.906666666666666]
["Twenthe0620","Twenthe","06","20",3.2466666666666666,17.080000000000002]
["Twenthe0621","Twenthe","06","21",3.1466666666666669,16.206666666666667]
["Twenthe0622","Twenthe","06","22",3.3599999999999994,15.946666666666665]
["Twenthe0623","Twenthe","06","23",3.6533333333333333,16.100000000000001]
["Twenthe0624","Twenthe","06","24",3.4066666666666663,16.3]
["Twenthe0625","Twenthe","06","25",3.3533333333333326,15.693333333333332]
["Twenthe0626","Twenthe","06","26",3.126666666666666,16.213333333333335]
["Twenthe0627","Twenthe","06","27",3.3400000000000003,17.386666666666663]
["Twenthe0628","Twenthe","06","28",3.2,17.466666666666665]
["Twenthe0629","Twenthe","06","29",2.9666666666666668,16.720000000000002]
["Twenthe0630","Twenthe","06","30",2.7066666666666666,17.09333333333333]
["Twenthe0701","Twenthe","07","01",2.9066666666666667,16.786666666666665]
["Twenthe0702","Twenthe","07","02",2.9399999999999995,18.000000000000004]
["Twenthe0703","Twenthe","07","03",3.1733333333333333,18.040000000000003]
["Twenthe0704","Twenthe","07","04",3.2000000000000006,18.186666666666667]
["Twenthe0705","Twenthe","07","05",2.8066666666666666,18.286666666666669]
["Twenthe0706","Twenthe","07","06",3.1266666666666656,17.760000000000002]
["Twenthe0707","Twenthe","07","07",3.1,17.293333333333337]
["Twenthe0708","Twenthe","07","08",3.1600000000000006,17.079999999999998]
["Twenthe0709","Twenthe","07","09",3.1533333333333333,17.113333333333337]
["Twenthe0710","Twenthe","07","10",3.1199999999999997,17.286666666666669]
["Twenthe0711","Twenthe","07","11",3.5799999999999992,17.073333333333334]
["Twenthe0712","Twenthe","07","12",3.22,16.5]
["Twenthe0713","Twenthe","07","13",2.9266666666666663,17.000000000000004]
["Twenthe0714","Twenthe","07","14",3.3933333333333326,17.5]
["Twenthe0715","Twenthe","07","15",3.3266666666666662,18.213333333333331]
["Twenthe0716","Twenthe","07","16",2.9266666666666672,18.646666666666665]
["Twenthe0717","Twenthe","07","17",3.1599999999999997,18.040000000000003]
["Twenthe0718","Twenthe","07","18",3.4066666666666667,18.16]
["Twenthe0719","Twenthe","07","19",3.1466666666666665,18.653333333333332]
["Twenthe0720","Twenthe","07","20",2.9866666666666672,18.3]
["Twenthe0721","Twenthe","07","21",3.0400000000000005,17.953333333333333]
["Twenthe0722","Twenthe","07","22",2.6866666666666661,18.033333333333339]
["Twenthe0723","Twenthe","07","23",2.88,18.260000000000002]
["Twenthe0724","Twenthe","07","24",2.9733333333333336,18.006666666666664]
["Twenthe0725","Twenthe","07","25",2.6066666666666669,18.353333333333339]
["Twenthe0726","Twenthe","07","26",2.4133333333333336,18.606666666666669]
["Twenthe0727","Twenthe","07","27",2.4133333333333336,19.853333333333335]
["Twenthe0728","Twenthe","07","28",2.4866666666666668,19.239999999999998]
["Twenthe0729","Twenthe","07","29",2.38,18.953333333333333]
["Twenthe0730","Twenthe","07","30",3.26,18.193333333333332]
["Twenthe0731","Twenthe","07","31",2.5600000000000005,17.953333333333333]
["Twenthe0801","Twenthe","08","01",2.3800000000000003,18.953333333333333]
["Twenthe0802","Twenthe","08","02",2.5,19.026666666666664]
["Twenthe0803","Twenthe","08","03",2.5333333333333328,18.040000000000003]
["Twenthe0804","Twenthe","08","04",2.54,18.186666666666664]
["Twenthe0805","Twenthe","08","05",2.5066666666666668,18.90666666666667]
["Twenthe0806","Twenthe","08","06",2.746666666666667,19.133333333333333]
["Twenthe0807","Twenthe","08","07",2.74,18.486666666666668]
["Twenthe0808","Twenthe","08","08",3.0666666666666669,17.753333333333334]
["Twenthe0809","Twenthe","08","09",2.9266666666666667,17.353333333333335]
["Twenthe0810","Twenthe","08","10",3.1799999999999997,17.366666666666667]
["Twenthe0811","Twenthe","08","11",3.0933333333333333,17.233333333333334]
["Twenthe0812","Twenthe","08","12",2.9533333333333331,17.113333333333333]
["Twenthe0813","Twenthe","08","13",3.2266666666666661,17.020000000000003]
["Twenthe0814","Twenthe","08","14",2.8400000000000003,17.793333333333337]
["Twenthe0815","Twenthe","08","15",3.0933333333333333,18.126666666666665]
["Twenthe0816","Twenthe","08","16",2.3933333333333331,17.36]
["Twenthe0817","Twenthe","08","17",2.9200000000000004,17.726666666666667]
["Twenthe0818","Twenthe","08","18",3.0933333333333328,18.7]
["Twenthe0819","Twenthe","08","19",3.2866666666666666,18.686666666666667]
["Twenthe0820","Twenthe","08","20",2.626666666666666,17.760000000000002]
["Twenthe0821","Twenthe","08","21",2.6466666666666669,16.993333333333332]
["Twenthe0822","Twenthe","08","22",2.7466666666666666,16.793333333333333]
["Twenthe0823","Twenthe","08","23",2.4533333333333331,16.833333333333332]
["Twenthe0824","Twenthe","08","24",2.6399999999999997,17.146666666666668]
["Twenthe0825","Twenthe","08","25",2.6066666666666669,17.153333333333332]
["Twenthe0826","Twenthe","08","26",3.2600000000000002,17.040000000000003]
["Twenthe0827","Twenthe","08","27",2.8933333333333326,16.040000000000003]
["Twenthe0828","Twenthe","08","28",2.9066666666666667,15.653333333333334]
["Twenthe0829","Twenthe","08","29",2.8800000000000008,14.726666666666665]
["Twenthe0830","Twenthe","08","30",2.8933333333333331,14.926666666666668]
["Twenthe0831","Twenthe","08","31",3.0799999999999992,15.353333333333335]
["Twenthe0901","Twenthe","09","01",2.6066666666666669,14.733333333333333]
["Twenthe0902","Twenthe","09","02",2.8400000000000003,15.466666666666667]
["Twenthe0903","Twenthe","09","03",3.0999999999999996,15.826666666666664]
["Twenthe0904","Twenthe","09","04",2.9733333333333323,15.879999999999997]
["Twenthe0905","Twenthe","09","05",2.7,16.266666666666669]
["Twenthe0906","Twenthe","09","06",3.26,16.573333333333334]
["Twenthe0907","Twenthe","09","07",3.28,15.913333333333332]
["Twenthe0908","Twenthe","09","08",3.0133333333333336,15.513333333333334]
["Twenthe0909","Twenthe","09","09",2.7666666666666662,15.853333333333335]
["Twenthe0910","Twenthe","09","10",3.0999999999999996,15.83333333333333]
["Twenthe0911","Twenthe","09","11",2.9999999999999996,15.786666666666669]
["Twenthe0912","Twenthe","09","12",3.0399999999999996,15.033333333333333]
["Twenthe0913","Twenthe","09","13",2.9266666666666667,14.319999999999999]
["Twenthe0914","Twenthe","09","14",3.5333333333333328,14.473333333333334]
["Twenthe0915","Twenthe","09","15",3.0266666666666664,13.866666666666665]
["Twenthe0916","Twenthe","09","16",2.9533333333333331,13.693333333333333]
["Twenthe0917","Twenthe","09","17",2.7199999999999998,13.466666666666667]
["Twenthe0918","Twenthe","09","18",2.5466666666666669,13.360000000000001]
["Twenthe0919","Twenthe","09","19",2.8933333333333331,13.093333333333334]
["Twenthe0920","Twenthe","09","20",2.9999999999999996,13.553333333333336]
["Twenthe0921","Twenthe","09","21",2.7133333333333334,13.453333333333337]
["Twenthe0922","Twenthe","09","22",3.1066666666666665,13.886666666666667]
["Twenthe0923","Twenthe","09","23",2.68,13.086666666666666]
["Twenthe0924","Twenthe","09","24",2.8533333333333339,12.92]
["Twenthe0925","Twenthe","09","25",2.6066666666666669,12.593333333333332]
["Twenthe0926","Twenthe","09","26",2.4066666666666667,12.546666666666669]
["Twenthe0927","Twenthe","09","27",2.3866666666666663,12.653333333333334]
["Twenthe0928","Twenthe","09","28",2.726666666666667,13.286666666666667]
["Twenthe0929","Twenthe","09","29",3.0133333333333336,13.193333333333333]
["Twenthe0930","Twenthe","09","30",2.8666666666666671,12.713333333333331]
["Twenthe1001","Twenthe","10","01",3.1333333333333329,12.860000000000001]
["Twenthe1002","Twenthe","10","02",3.1599999999999997,12.74]
["Twenthe1003","Twenthe","10","03",3.2800000000000002,13.32]
["Twenthe1004","Twenthe","10","04",3.3800000000000008,12.95333333333333]
["Twenthe1005","Twenthe","10","05",3.4133333333333336,12.593333333333334]
["Twenthe1006","Twenthe","10","06",3.4066666666666667,11.966666666666667]
["Twenthe1007","Twenthe","10","07",3.2666666666666666,11.326666666666666]
["Twenthe1008","Twenthe","10","08",2.7399999999999998,10.513333333333334]
["Twenthe1009","Twenthe","10","09",3.1,10.893333333333334]
["Twenthe1010","Twenthe","10","10",3.54,11.120000000000001]
["Twenthe1011","Twenthe","10","11",3.4466666666666668,10.746666666666668]
["Twenthe1012","Twenthe","10","12",2.813333333333333,10.273333333333333]
["Twenthe1013","Twenthe","10","13",2.253333333333333,10.42]
["Twenthe1014","Twenthe","10","14",2.5999999999999996,9.82]
["Twenthe1015","Twenthe","10","15",3.02,10.053333333333335]
["Twenthe1016","Twenthe","10","16",3.6666666666666656,9.946666666666669]
["Twenthe1017","Twenthe","10","17",3.4866666666666664,9.56]
["Twenthe1018","Twenthe","10","18",3.2466666666666666,9.7799999999999994]
["Twenthe1019","Twenthe","10","19",3.1466666666666669,10.18]
["Twenthe1020","Twenthe","10","20",3.3800000000000003,10.4]
["Twenthe1021","Twenthe","10","21",3.8266666666666667,10.640000000000002]
["Twenthe1022","Twenthe","10","22",3.58,10.58]
["Twenthe1023","Twenthe","10","23",3.94,10.246666666666664]
["Twenthe1024","Twenthe","10","24",4.0066666666666668,10.053333333333333]
["Twenthe1025","Twenthe","10","25",4.1800000000000006,10.686666666666667]
["Twenthe1026","Twenthe","10","26",4.2333333333333334,10.533333333333333]
["Twenthe1027","Twenthe","10","27",3.9733333333333336,9.3666666666666654]
["Twenthe1028","Twenthe","10","28",3.6866666666666665,9.42]
["Twenthe1029","Twenthe","10","29",3.5,9.6066666666666656]
["Twenthe1030","Twenthe","10","30",3.26,9.92]
["Twenthe1031","Twenthe","10","31",3.5333333333333328,9.4333333333333353]
["Twenthe1101","Twenthe","11","01",3.6733333333333333,9.2466666666666661]
["Twenthe1102","Twenthe","11","02",3.773333333333333,9.8933333333333344]
["Twenthe1103","Twenthe","11","03",3.94,9.9533333333333349]
["Twenthe1104","Twenthe","11","04",3.4066666666666667,9.4]
["Twenthe1105","Twenthe","11","05",3.5000000000000004,8.2333333333333325]
["Twenthe1106","Twenthe","11","06",3.7199999999999998,8.2733333333333317]
["Twenthe1107","Twenthe","11","07",3.5999999999999996,7.84]
["Twenthe1108","Twenthe","11","08",3.8200000000000003,7.4866666666666672]
["Twenthe1109","Twenthe","11","09",3.8466666666666658,6.62]
["Twenthe1110","Twenthe","11","10",3.5533333333333332,6.46]
["Twenthe1111","Twenthe","11","11",4.4000000000000004,6.8133333333333344]
["Twenthe1112","Twenthe","11","12",4.0133333333333336,7.0533333333333337]
["Twenthe1113","Twenthe","11","13",3.0266666666666664,6.9399999999999995]
["Twenthe1114","Twenthe","11","14",3.3,6.88]
["Twenthe1115","Twenthe","11","15",3.0533333333333332,6.0466666666666669]
["Twenthe1116","Twenthe","11","16",2.8866666666666663,6.4066666666666681]
["Twenthe1117","Twenthe","11","17",3.1399999999999997,6.5999999999999988]
["Twenthe1118","Twenthe","11","18",3.36,6.3800000000000008]
["Twenthe1119","Twenthe","11","19",3.1599999999999993,5.8933333333333326]
["Twenthe1120","Twenthe","11","20",3.4799999999999995,6.3199999999999994]
["Twenthe1121","Twenthe","11","21",3.5399999999999996,5.7866666666666671]
["Twenthe1122","Twenthe","11","22",3.9533333333333327,6.3266666666666662]
["Twenthe1123","Twenthe","11","23",3.3533333333333335,6.3599999999999994]
["Twenthe1124","Twenthe","11","24",3.0933333333333333,5.44]
["Twenthe1125","Twenthe","11","25",3.813333333333333,5.5333333333333341]
["Twenthe1126","Twenthe","11","26",3.6133333333333328,5.0933333333333337]
["Twenthe1127","Twenthe","11","27",3.3199999999999994,5.4266666666666659]
["Twenthe1128","Twenthe","11","28",3.1533333333333329,5.3400000000000007]
["Twenthe1129","Twenthe","11","29",3.4799999999999991,5.3666666666666654]
["Twenthe1130","Twenthe","11","30",2.9133333333333336,4.620000000000001]
["Twenthe1201","Twenthe","12","01",3.9533333333333336,5.0866666666666669]
["Twenthe1202","Twenthe","12","02",3.4133333333333336,4.2666666666666666]
["Twenthe1203","Twenthe","12","03",3.6333333333333333,4.2]
["Twenthe1204","Twenthe","12","04",4.18,4.5466666666666669]
["Twenthe1205","Twenthe","12","05",4.4933333333333332,5.7133333333333338]
["Twenthe1206","Twenthe","12","06",4.0733333333333324,5.073333333333335]
["Twenthe1207","Twenthe","12","07",4.2133333333333329,3.82]
["Twenthe1208","Twenthe","12","08",3.9933333333333332,3.2466666666666666]
["Twenthe1209","Twenthe","12","09",3.7866666666666666,2.7666666666666666]
["Twenthe1210","Twenthe","12","10",3.3933333333333331,2.3133333333333335]
["Twenthe1211","Twenthe","12","11",4.0333333333333332,2.9666666666666668]
["Twenthe1212","Twenthe","12","12",3.6799999999999997,3.3600000000000008]
["Twenthe1213","Twenthe","12","13",3.9666666666666663,2.726666666666667]
["Twenthe1214","Twenthe","12","14",3.8866666666666663,2.2666666666666666]
["Twenthe1215","Twenthe","12","15",4.4666666666666659,3.1333333333333333]
["Twenthe1216","Twenthe","12","16",4.2399999999999993,2.9666666666666668]
["Twenthe1217","Twenthe","12","17",3.4066666666666663,2.3466666666666667]
["Twenthe1218","Twenthe","12","18",3.0333333333333332,1.8]
["Twenthe1219","Twenthe","12","19",3.28,1.1333333333333333]
["Twenthe1220","Twenthe","12","20",4.0333333333333332,1.4]
["Twenthe1221","Twenthe","12","21",3.94,1.9]
["Twenthe1222","Twenthe","12","22",4.04,3.0466666666666664]
["Twenthe1223","Twenthe","12","23",4.3,3.6866666666666665]
["Twenthe1224","Twenthe","12","24",4.8,4.4599999999999982]
["Twenthe1225","Twenthe","12","25",4.08,3.9999999999999996]
["Twenthe1226","Twenthe","12","26",3.5733333333333328,2.7133333333333334]
["Twenthe1227","Twenthe","12","27",4.4933333333333341,2.8666666666666671]
["Twenthe1228","Twenthe","12","28",4.4466666666666663,2.726666666666667]
["Twenthe1229","Twenthe","12","29",4.12,2.2533333333333334]
["Twenthe1230","Twenthe","12","30",4.1199999999999992,2.0733333333333333]
["Twenthe1231","Twenthe","12","31",3.7666666666666662,2.2266666666666666]
["Vlissingen0101","Vlissingen","01","01",7.3,4.9666666666666677]
["Vlissingen0102","Vlissingen","01","02",7.0866666666666669,4.78]
["Vlissingen0103","Vlissingen","01","03",7.706666666666667,4.3066666666666666]
["Vlissingen0104","Vlissingen","01","04",8.08,4.8533333333333344]
["Vlissingen0105","Vlissingen","01","05",7.5200000000000005,4.4400000000000004]
["Vlissingen0106","Vlissingen","01","06",6.3533333333333344,4.7866666666666662]
["Vlissingen0107","Vlissingen","01","07",7.2266666666666648,5.046666666666666]
["Vlissingen0108","Vlissingen","01","08",7.3866666666666676,4.54]
["Vlissingen0109","Vlissingen","01","09",6.793333333333333,4.3133333333333335]
["Vlissingen0110","Vlissingen","01","10",6.56,4.253333333333333]
["Vlissingen0111","Vlissingen","01","11",7.8133333333333326,4.5133333333333336]
["Vlissingen0112","Vlissingen","01","12",7.839999999999999,4.2066666666666661]
["Vlissingen0113","Vlissingen","01","13",8.0933333333333319,4.7533333333333339]
["Vlissingen0114","Vlissingen","01","14",6.5666666666666673,4.4866666666666664]
["Vlissingen0115","Vlissingen","01","15",7.1799999999999979,4.1066666666666665]
["Vlissingen0116","Vlissingen","01","16",6.626666666666666,4.26]
["Vlissingen0117","Vlissingen","01","17",7.3800000000000008,4.6466666666666665]
["Vlissingen0118","Vlissingen","01","18",7.666666666666667,4.9399999999999995]
["Vlissingen0119","Vlissingen","01","19",7.8466666666666676,5.746666666666667]
["Vlissingen0120","Vlissingen","01","20",8.4066666666666663,5.6733333333333329]
["Vlissingen0121","Vlissingen","01","21",7.3866666666666667,5.2866666666666662]
["Vlissingen0122","Vlissingen","01","22",7.0133333333333336,4.6066666666666665]
["Vlissingen0123","Vlissingen","01","23",6.6333333333333337,4.2]
["Vlissingen0124","Vlissingen","01","24",5.3066666666666675,3.9266666666666663]
["Vlissingen0125","Vlissingen","01","25",6.166666666666667,3.4]
["Vlissingen0126","Vlissingen","01","26",7.4133333333333331,3.6400000000000006]
["Vlissingen0127","Vlissingen","01","27",6.9933333333333332,3.6733333333333329]
["Vlissingen0128","Vlissingen","01","28",7.5666666666666664,4.1733333333333338]
["Vlissingen0129","Vlissingen","01","29",7.1933333333333334,4.3599999999999994]
["Vlissingen0130","Vlissingen","01","30",6.64,4.2399999999999993]
["Vlissingen0131","Vlissingen","01","31",8.32,3.9666666666666663]
["Vlissingen0201","Vlissingen","02","01",7.8000000000000007,3.82]
["Vlissingen0202","Vlissingen","02","02",7.8266666666666653,4.38]
["Vlissingen0203","Vlissingen","02","03",6.4466666666666681,4.9200000000000008]
["Vlissingen0204","Vlissingen","02","04",7.879999999999999,5.3066666666666684]
["Vlissingen0205","Vlissingen","02","05",8.58,5.6133333333333324]
["Vlissingen0206","Vlissingen","02","06",6.98,5.4466666666666663]
["Vlissingen0207","Vlissingen","02","07",7.2066666666666652,4.5533333333333337]
["Vlissingen0208","Vlissingen","02","08",7.5466666666666669,4.7]
["Vlissingen0209","Vlissingen","02","09",6.8866666666666658,4.2866666666666662]
["Vlissingen0210","Vlissingen","02","10",7.4800000000000013,4.5133333333333336]
["Vlissingen0211","Vlissingen","02","11",7.0133333333333336,4.7266666666666675]
["Vlissingen0212","Vlissingen","02","12",7.0933333333333328,4.4733333333333327]
["Vlissingen0213","Vlissingen","02","13",5.6400000000000006,4.12]
["Vlissingen0214","Vlissingen","02","14",5.8466666666666667,3.78]
["Vlissingen0215","Vlissingen","02","15",6.5333333333333332,4.5466666666666669]
["Vlissingen0216","Vlissingen","02","16",5.72,4.3133333333333335]
["Vlissingen0217","Vlissingen","02","17",4.8933333333333335,3.9866666666666668]
["Vlissingen0218","Vlissingen","02","18",5.1133333333333333,4.1800000000000006]
["Vlissingen0219","Vlissingen","02","19",6.3866666666666667,4.24]
["Vlissingen0220","Vlissingen","02","20",6.0400000000000009,4.1933333333333334]
["Vlissingen0221","Vlissingen","02","21",6.3533333333333335,4.0599999999999996]
["Vlissingen0222","Vlissingen","02","22",7.3599999999999994,4.6133333333333333]
["Vlissingen0223","Vlissingen","02","23",6.86,4.6399999999999997]
["Vlissingen0224","Vlissingen","02","24",6.3599999999999994,4.993333333333335]
["Vlissingen0225","Vlissingen","02","25",6.626666666666666,5.0866666666666651]
["Vlissingen0226","Vlissingen","02","26",7.3266666666666653,5.2400000000000011]
["Vlissingen0227","Vlissingen","02","27",7.4200000000000008,4.92]
["Vlissingen0228","Vlissingen","02","28",6.4399999999999986,4.9266666666666667]
["Vlissingen0229","Vlissingen","02","29",7.0750000000000011,5.7]
["Vlissingen0301","Vlissingen","03","01",6.5533333333333337,4.7600000000000007]
["Vlissingen0302","Vlissingen","03","02",5.9533333333333331,4.6066666666666674]
["Vlissingen0303","Vlissingen","03","03",6.0533333333333337,4.5133333333333336]
["Vlissingen0304","Vlissingen","03","04",5.6066666666666682,4.453333333333334]
["Vlissingen0305","Vlissingen","03","05",5.1466666666666665,5.253333333333333]
["Vlissingen0306","Vlissingen","03","06",6.6733333333333329,5.5799999999999992]
["Vlissingen0307","Vlissingen","03","07",6.44,6.2266666666666675]
["Vlissingen0308","Vlissingen","03","08",6.8466666666666667,6.833333333333333]
["Vlissingen0309","Vlissingen","03","09",7.5533333333333328,6.666666666666667]
["Vlissingen0310","Vlissingen","03","10",7.4533333333333331,6.1733333333333329]
["Vlissingen0311","Vlissingen","03","11",6.9733333333333336,6.2133333333333329]
["Vlissingen0312","Vlissingen","03","12",6.1866666666666665,6.1933333333333334]
["Vlissingen0313","Vlissingen","03","13",5.453333333333334,6.2399999999999993]
["Vlissingen0314","Vlissingen","03","14",5.5866666666666669,6.38]
["Vlissingen0315","Vlissingen","03","15",6.0133333333333336,7.4600000000000017]
["Vlissingen0316","Vlissingen","03","16",5.9799999999999995,7.953333333333334]
["Vlissingen0317","Vlissingen","03","17",6.0600000000000005,7.26]
["Vlissingen0318","Vlissingen","03","18",6.7866666666666671,6.7399999999999993]
["Vlissingen0319","Vlissingen","03","19",5.8133333333333335,6.5533333333333319]
["Vlissingen0320","Vlissingen","03","20",6.1933333333333334,6.9399999999999995]
["Vlissingen0321","Vlissingen","03","21",6.1866666666666674,6.546666666666666]
["Vlissingen0322","Vlissingen","03","22",5.9133333333333322,6.9933333333333341]
["Vlissingen0323","Vlissingen","03","23",5.4933333333333341,7.0666666666666664]
["Vlissingen0324","Vlissingen","03","24",5.2666666666666657,7.1800000000000015]
["Vlissingen0325","Vlissingen","03","25",5.3733333333333322,7.2066666666666661]
["Vlissingen0326","Vlissingen","03","26",5.0133333333333328,7.42]
["Vlissingen0327","Vlissingen","03","27",5.2266666666666675,7.373333333333334]
["Vlissingen0328","Vlissingen","03","28",5.62,7.7399999999999993]
["Vlissingen0329","Vlissingen","03","29",4.879999999999999,8.1733333333333338]
["Vlissingen0330","Vlissingen","03","30",5.14,8.4733333333333327]
["Vlissingen0331","Vlissingen","03","31",5.9133333333333331,8.9]
["Vlissingen0401","Vlissingen","04","01",6.1466666666666647,9.4466666666666672]
["Vlissingen0402","Vlissingen","04","02",6.3466666666666667,10.026666666666667]
["Vlissingen0403","Vlissingen","04","03",5.6466666666666656,9.2733333333333352]
["Vlissingen0404","Vlissingen","04","04",6.4999999999999991,8.4799999999999986]
["Vlissingen0405","Vlissingen","04","05",6.5666666666666655,7.8533333333333335]
["Vlissingen0406","Vlissingen","04","06",6.4733333333333345,8.2666666666666675]
["Vlissingen0407","Vlissingen","04","07",5.5133333333333336,8.0133333333333319]
["Vlissingen0408","Vlissingen","04","08",5.5666666666666664,7.7866666666666671]
["Vlissingen0409","Vlissingen","04","09",5.24,8.1733333333333356]
["Vlissingen0410","Vlissingen","04","10",5.0999999999999996,8.4733333333333345]
["Vlissingen0411","Vlissingen","04","11",5.0733333333333333,8.76]
["Vlissingen0412","Vlissingen","04","12",5.6866666666666683,8.9066666666666663]
["Vlissingen0413","Vlissingen","04","13",5.8933333333333326,9.1533333333333342]
["Vlissingen0414","Vlissingen","04","14",5.246666666666667,9.6733333333333338]
["Vlissingen0415","Vlissingen","04","15",5.26,10.226666666666668]
["Vlissingen0416","Vlissingen","04","16",5.0733333333333341,9.9600000000000009]
["Vlissingen0417","Vlissingen","04","17",5.6266666666666669,9.8133333333333326]
["Vlissingen0418","Vlissingen","04","18",6.8333333333333321,9.7199999999999989]
["Vlissingen0419","Vlissingen","04","19",5.3199999999999994,9.5733333333333324]
["Vlissingen0420","Vlissingen","04","20",4.8266666666666671,10.413333333333332]
["Vlissingen0421","Vlissingen","04","21",4.5133333333333336,10.893333333333333]
["Vlissingen0422","Vlissingen","04","22",4.28,11.24]
["Vlissingen0423","Vlissingen","04","23",3.8733333333333335,11.426666666666669]
["Vlissingen0424","Vlissingen","04","24",4.3066666666666666,12.466666666666669]
["Vlissingen0425","Vlissingen","04","25",5.2333333333333334,12.606666666666666]
["Vlissingen0426","Vlissingen","04","26",5.8199999999999994,11.78]
["Vlissingen0427","Vlissingen","04","27",5.8666666666666654,12.113333333333333]
["Vlissingen0428","Vlissingen","04","28",5.6,11.973333333333333]
["Vlissingen0429","Vlissingen","04","29",5.6533333333333342,12.213333333333335]
["Vlissingen0430","Vlissingen","04","30",5.6733333333333329,12.34]
["Vlissingen0501","Vlissingen","05","01",5.8466666666666658,12.359999999999998]
["Vlissingen0502","Vlissingen","05","02",5.3866666666666667,11.426666666666668]
["Vlissingen0503","Vlissingen","05","03",5.4933333333333341,11.206666666666667]
["Vlissingen0504","Vlissingen","05","04",6.0466666666666669,11.3]
["Vlissingen0505","Vlissingen","05","05",5.8533333333333326,11.819999999999999]
["Vlissingen0506","Vlissingen","05","06",5.2866666666666662,12.860000000000001]
["Vlissingen0507","Vlissingen","05","07",5.8866666666666676,13.04]
["Vlissingen0508","Vlissingen","05","08",6.2733333333333343,13.12]
["Vlissingen0509","Vlissingen","05","09",5.3866666666666667,13.319999999999999]
["Vlissingen0510","Vlissingen","05","10",5.7999999999999989,13.740000000000002]
["Vlissingen0511","Vlissingen","05","11",6.3199999999999985,12.919999999999998]
["Vlissingen0512","Vlissingen","05","12",6.0333333333333332,12.626666666666669]
["Vlissingen0513","Vlissingen","05","13",5.4266666666666659,13.246666666666666]
["Vlissingen0514","Vlissingen","05","14",5.7266666666666657,12.553333333333335]
["Vlissingen0515","Vlissingen","05","15",4.6933333333333334,12.906666666666668]
["Vlissingen0516","Vlissingen","05","16",5.2199999999999989,13.059999999999999]
["Vlissingen0517","Vlissingen","05","17",5.8066666666666658,13.146666666666665]
["Vlissingen0518","Vlissingen","05","18",6.1066666666666665,13.293333333333333]
["Vlissingen0519","Vlissingen","05","19",5.8933333333333335,13.426666666666666]
["Vlissingen0520","Vlissingen","05","20",5.4599999999999991,13.553333333333333]
["Vlissingen0521","Vlissingen","05","21",5.6599999999999993,13.680000000000001]
["Vlissingen0522","Vlissingen","05","22",6.5133333333333328,13.59333333333333]
["Vlissingen0523","Vlissingen","05","23",5.4,13.846666666666666]
["Vlissingen0524","Vlissingen","05","24",5.6533333333333333,14.226666666666668]
["Vlissingen0525","Vlissingen","05","25",5.4666666666666668,14.853333333333333]
["Vlissingen0526","Vlissingen","05","26",6.4466666666666672,14.446666666666667]
["Vlissingen0527","Vlissingen","05","27",5.7733333333333343,14.419999999999998]
["Vlissingen0528","Vlissingen","05","28",6.4999999999999991,14.706666666666667]
["Vlissingen0529","Vlissingen","05","29",5.96,14.3]
["Vlissingen0530","Vlissingen","05","30",5.0066666666666659,14.193333333333333]
["Vlissingen0531","Vlissingen","05","31",4.8666666666666663,14.106666666666666]
["Vlissingen0601","Vlissingen","06","01",4.166666666666667,14.706666666666667]
["Vlissingen0602","Vlissingen","06","02",4.9000000000000012,14.986666666666668]
["Vlissingen0603","Vlissingen","06","03",4.9866666666666664,15.006666666666664]
["Vlissingen0604","Vlissingen","06","04",5.6066666666666665,15.02]
["Vlissingen0605","Vlissingen","06","05",4.9866666666666664,14.979999999999997]
["Vlissingen0606","Vlissingen","06","06",5.3533333333333335,14.993333333333332]
["Vlissingen0607","Vlissingen","06","07",4.8199999999999994,15.353333333333332]
["Vlissingen0608","Vlissingen","06","08",5.3,15.900000000000002]
["Vlissingen0609","Vlissingen","06","09",5.0200000000000005,16.033333333333331]
["Vlissingen0610","Vlissingen","06","10",4.2866666666666653,15.540000000000001]
["Vlissingen0611","Vlissingen","06","11",5.12,15.253333333333332]
["Vlissingen0612","Vlissingen","06","12",5.1733333333333329,15.546666666666669]
["Vlissingen0613","Vlissingen","06","13",5.0733333333333341,15.640000000000002]
["Vlissingen0614","Vlissingen","06","14",4.8599999999999994,16.226666666666667]
["Vlissingen0615","Vlissingen","06","15",5.66,15.833333333333332]
["Vlissingen0616","Vlissingen","06","16",5.2866666666666671,15.813333333333333]
["Vlissingen0617","Vlissingen","06","17",5.5866666666666669,17.126666666666669]
["Vlissingen0618","Vlissingen","06","18",5.5733333333333333,17.000000000000004]
["Vlissingen0619","Vlissingen","06","19",5.9266666666666659,16.986666666666668]
["Vlissingen0620","Vlissingen","06","20",4.9466666666666672,16.839999999999996]
["Vlissingen0621","Vlissingen","06","21",5.3533333333333335,16.40666666666667]
["Vlissingen0622","Vlissingen","06","22",6.4933333333333332,16.439999999999998]
["Vlissingen0623","Vlissingen","06","23",6.8400000000000007,16.846666666666664]
["Vlissingen0624","Vlissingen","06","24",5.7133333333333329,16.913333333333334]
["Vlissingen0625","Vlissingen","06","25",5.2600000000000007,16.780000000000005]
["Vlissingen0626","Vlissingen","06","26",4.6799999999999988,17.27333333333333]
["Vlissingen0627","Vlissingen","06","27",5.3466666666666658,17.433333333333334]
["Vlissingen0628","Vlissingen","06","28",5.2666666666666666,17.393333333333331]
["Vlissingen0629","Vlissingen","06","29",5.08,16.973333333333336]
["Vlissingen0630","Vlissingen","06","30",5.0933333333333328,17.406666666666663]
["Vlissingen0701","Vlissingen","07","01",5.9133333333333331,17.566666666666666]
["Vlissingen0702","Vlissingen","07","02",5.1933333333333325,18.293333333333333]
["Vlissingen0703","Vlissingen","07","03",5.4866666666666664,18.006666666666668]
["Vlissingen0704","Vlissingen","07","04",5.6266666666666678,18.313333333333333]
["Vlissingen0705","Vlissingen","07","05",5.293333333333333,18.173333333333332]
["Vlissingen0706","Vlissingen","07","06",5.6,17.633333333333333]
["Vlissingen0707","Vlissingen","07","07",6.2999999999999989,17.38]
["Vlissingen0708","Vlissingen","07","08",5.8066666666666666,17.286666666666669]
["Vlissingen0709","Vlissingen","07","09",6.626666666666666,17.353333333333335]
["Vlissingen0710","Vlissingen","07","10",5.9866666666666664,17.513333333333332]
["Vlissingen0711","Vlissingen","07","11",6.5066666666666659,17.040000000000003]
["Vlissingen0712","Vlissingen","07","12",5.666666666666667,16.786666666666669]
["Vlissingen0713","Vlissingen","07","13",5.1333333333333337,17.220000000000002]
["Vlissingen0714","Vlissingen","07","14",5.8466666666666667,17.506666666666668]
["Vlissingen0715","Vlissingen","07","15",5.5600000000000005,18.213333333333335]
["Vlissingen0716","Vlissingen","07","16",5.1266666666666669,18.46]
["Vlissingen0717","Vlissingen","07","17",6.133333333333332,18.306666666666668]
["Vlissingen0718","Vlissingen","07","18",6.5000000000000009,18.346666666666668]
["Vlissingen0719","Vlissingen","07","19",5.6533333333333333,19.113333333333333]
["Vlissingen0720","Vlissingen","07","20",4.76,18.446666666666665]
["Vlissingen0721","Vlissingen","07","21",4.8199999999999994,18.2]
["Vlissingen0722","Vlissingen","07","22",4.4466666666666672,18.580000000000002]
["Vlissingen0723","Vlissingen","07","23",4.8400000000000007,18.733333333333334]
["Vlissingen0724","Vlissingen","07","24",5.4533333333333331,18.893333333333331]
["Vlissingen0725","Vlissingen","07","25",5.1800000000000006,18.93333333333333]
["Vlissingen0726","Vlissingen","07","26",4.2666666666666675,19.02]
["Vlissingen0727","Vlissingen","07","27",3.9933333333333332,19.40666666666667]
["Vlissingen0728","Vlissingen","07","28",4.4866666666666672,19.606666666666673]
["Vlissingen0729","Vlissingen","07","29",4.7266666666666657,19.5]
["Vlissingen0730","Vlissingen","07","30",5.6800000000000015,18.766666666666666]
["Vlissingen0731","Vlissingen","07","31",4.5599999999999996,18.64]
["Vlissingen0801","Vlissingen","08","01",4.4666666666666677,19.3]
["Vlissingen0802","Vlissingen","08","02",5.0533333333333337,19.259999999999998]
["Vlissingen0803","Vlissingen","08","03",5.0733333333333341,18.700000000000003]
["Vlissingen0804","Vlissingen","08","04",5.1799999999999988,18.940000000000001]
["Vlissingen0805","Vlissingen","08","05",4.6066666666666665,19.48]
["Vlissingen0806","Vlissingen","08","06",4.9400000000000004,19.406666666666663]
["Vlissingen0807","Vlissingen","08","07",5.2133333333333347,18.599999999999998]
["Vlissingen0808","Vlissingen","08","08",5.4066666666666663,18.086666666666666]
["Vlissingen0809","Vlissingen","08","09",4.833333333333333,18.286666666666672]
["Vlissingen0810","Vlissingen","08","10",6.02,18.453333333333333]
["Vlissingen0811","Vlissingen","08","11",5.5400000000000009,18.533333333333335]
["Vlissingen0812","Vlissingen","08","12",5.74,18.273333333333333]
["Vlissingen0813","Vlissingen","08","13",6.0533333333333319,18.313333333333333]
["Vlissingen0814","Vlissingen","08","14",4.8066666666666666,18.433333333333337]
["Vlissingen0815","Vlissingen","08","15",5.4,18.826666666666664]
["Vlissingen0816","Vlissingen","08","16",5.3733333333333331,18.579999999999998]
["Vlissingen0817","Vlissingen","08","17",5.9866666666666664,18.766666666666666]
["Vlissingen0818","Vlissingen","08","18",5.5266666666666673,19.440000000000001]
["Vlissingen0819","Vlissingen","08","19",5.7,18.980000000000004]
["Vlissingen0820","Vlissingen","08","20",5.6533333333333324,18.173333333333336]
["Vlissingen0821","Vlissingen","08","21",5.2266666666666657,17.95333333333333]
["Vlissingen0822","Vlissingen","08","22",5.0733333333333333,17.88]
["Vlissingen0823","Vlissingen","08","23",5.0733333333333333,18.513333333333332]
["Vlissingen0824","Vlissingen","08","24",5.26,18.086666666666666]
["Vlissingen0825","Vlissingen","08","25",5.62,18.106666666666666]
["Vlissingen0826","Vlissingen","08","26",5.8866666666666667,18.100000000000005]
["Vlissingen0827","Vlissingen","08","27",5.7133333333333338,17.380000000000003]
["Vlissingen0828","Vlissingen","08","28",5.7266666666666675,17.166666666666668]
["Vlissingen0829","Vlissingen","08","29",5.7,17.006666666666668]
["Vlissingen0830","Vlissingen","08","30",5.7733333333333325,17.073333333333331]
["Vlissingen0831","Vlissingen","08","31",5.046666666666666,17.100000000000001]
["Vlissingen0901","Vlissingen","09","01",5.133333333333332,16.846666666666668]
["Vlissingen0902","Vlissingen","09","02",5.6066666666666665,17.226666666666667]
["Vlissingen0903","Vlissingen","09","03",5.6000000000000005,17.600000000000001]
["Vlissingen0904","Vlissingen","09","04",4.9333333333333327,17.373333333333331]
["Vlissingen0905","Vlissingen","09","05",5.44,17.846666666666671]
["Vlissingen0906","Vlissingen","09","06",6.1933333333333334,17.733333333333334]
["Vlissingen0907","Vlissingen","09","07",6.0733333333333341,17.253333333333334]
["Vlissingen0908","Vlissingen","09","08",4.7666666666666657,17.246666666666666]
["Vlissingen0909","Vlissingen","09","09",5.2800000000000011,17.160000000000004]
["Vlissingen0910","Vlissingen","09","10",5.5533333333333337,17.133333333333333]
["Vlissingen0911","Vlissingen","09","11",5.4,17.273333333333333]
["Vlissingen0912","Vlissingen","09","12",5.8999999999999995,16.733333333333334]
["Vlissingen0913","Vlissingen","09","13",5.6799999999999988,16.386666666666667]
["Vlissingen0914","Vlissingen","09","14",6.7866666666666671,16.326666666666664]
["Vlissingen0915","Vlissingen","09","15",5.5866666666666678,16.320000000000004]
["Vlissingen0916","Vlissingen","09","16",5.6866666666666665,15.833333333333334]
["Vlissingen0917","Vlissingen","09","17",4.9399999999999995,15.393333333333334]
["Vlissingen0918","Vlissingen","09","18",5.1066666666666665,15.320000000000002]
["Vlissingen0919","Vlissingen","09","19",5.6666666666666661,15.593333333333334]
["Vlissingen0920","Vlissingen","09","20",5.62,15.966666666666665]
["Vlissingen0921","Vlissingen","09","21",4.753333333333333,16.000000000000004]
["Vlissingen0922","Vlissingen","09","22",5.2466666666666679,15.960000000000003]
["Vlissingen0923","Vlissingen","09","23",4.8733333333333331,15.58]
["Vlissingen0924","Vlissingen","09","24",5.2399999999999993,14.973333333333333]
["Vlissingen0925","Vlissingen","09","25",5.1599999999999993,14.846666666666666]
["Vlissingen0926","Vlissingen","09","26",5.0733333333333324,15.006666666666666]
["Vlissingen0927","Vlissingen","09","27",4.4333333333333336,14.9]
["Vlissingen0928","Vlissingen","09","28",5.2866666666666662,15.406666666666666]
["Vlissingen0929","Vlissingen","09","29",5.0999999999999996,15.366666666666667]
["Vlissingen0930","Vlissingen","09","30",5.8333333333333321,15.206666666666667]
["Vlissingen1001","Vlissingen","10","01",6.3266666666666662,15.22]
["Vlissingen1002","Vlissingen","10","02",6.2666666666666666,14.966666666666669]
["Vlissingen1003","Vlissingen","10","03",6.26,15.073333333333331]
["Vlissingen1004","Vlissingen","10","04",6.5133333333333345,14.633333333333335]
["Vlissingen1005","Vlissingen","10","05",6.28,14.126666666666667]
["Vlissingen1006","Vlissingen","10","06",6.7666666666666666,13.973333333333331]
["Vlissingen1007","Vlissingen","10","07",6.120000000000001,13.246666666666666]
["Vlissingen1008","Vlissingen","10","08",5.9399999999999995,13.326666666666663]
["Vlissingen1009","Vlissingen","10","09",6.0733333333333324,13.426666666666666]
["Vlissingen1010","Vlissingen","10","10",6.88,13.446666666666665]
["Vlissingen1011","Vlissingen","10","11",6.6599999999999993,13.013333333333334]
["Vlissingen1012","Vlissingen","10","12",5.9200000000000008,13.093333333333332]
["Vlissingen1013","Vlissingen","10","13",5.6800000000000006,12.913333333333332]
["Vlissingen1014","Vlissingen","10","14",5.7266666666666675,12.353333333333332]
["Vlissingen1015","Vlissingen","10","15",5.9066666666666663,12.226666666666667]
["Vlissingen1016","Vlissingen","10","16",6.580000000000001,12.240000000000002]
["Vlissingen1017","Vlissingen","10","17",6.166666666666667,12.086666666666668]
["Vlissingen1018","Vlissingen","10","18",6.2533333333333339,12.013333333333334]
["Vlissingen1019","Vlissingen","10","19",6.06,12.346666666666668]
["Vlissingen1020","Vlissingen","10","20",6.9733333333333327,12.146666666666668]
["Vlissingen1021","Vlissingen","10","21",7.3866666666666667,12.266666666666664]
["Vlissingen1022","Vlissingen","10","22",6.96,12.226666666666667]
["Vlissingen1023","Vlissingen","10","23",7.5666666666666655,12.006666666666668]
["Vlissingen1024","Vlissingen","10","24",7.4466666666666663,11.54]
["Vlissingen1025","Vlissingen","10","25",7.7999999999999989,12.233333333333333]
["Vlissingen1026","Vlissingen","10","26",7.4399999999999986,12.04]
["Vlissingen1027","Vlissingen","10","27",7.453333333333334,11.553333333333336]
["Vlissingen1028","Vlissingen","10","28",6.9466666666666681,11.653333333333334]
["Vlissingen1029","Vlissingen","10","29",6.5533333333333328,11.273333333333335]
["Vlissingen1030","Vlissingen","10","30",6.1266666666666652,11.346666666666669]
["Vlissingen1031","Vlissingen","10","31",6.4733333333333336,11.346666666666668]
["Vlissingen1101","Vlissingen","11","01",6.8999999999999995,11.026666666666669]
["Vlissingen1102","Vlissingen","11","02",7.0933333333333328,10.926666666666668]
["Vlissingen1103","Vlissingen","11","03",7.6999999999999993,11.333333333333334]
["Vlissingen1104","Vlissingen","11","04",6.8800000000000008,10.633333333333335]
["Vlissingen1105","Vlissingen","11","05",6.6000000000000023,10.4]
["Vlissingen1106","Vlissingen","11","06",7.0066666666666659,10.56]
["Vlissingen1107","Vlissingen","11","07",6.9333333333333327,9.8333333333333321]
["Vlissingen1108","Vlissingen","11","08",8.2333333333333325,9.3933333333333326]
["Vlissingen1109","Vlissingen","11","09",6.62,8.9266666666666659]
["Vlissingen1110","Vlissingen","11","10",6.6133333333333324,9.1866666666666674]
["Vlissingen1111","Vlissingen","11","11",8.0266666666666673,8.9133333333333322]
["Vlissingen1112","Vlissingen","11","12",7.4266666666666667,9.3666666666666671]
["Vlissingen1113","Vlissingen","11","13",6.4133333333333322,9.4]
["Vlissingen1114","Vlissingen","11","14",6.7333333333333325,8.94]
["Vlissingen1115","Vlissingen","11","15",5.2266666666666675,8.293333333333333]
["Vlissingen1116","Vlissingen","11","16",5.1866666666666665,8.1933333333333334]
["Vlissingen1117","Vlissingen","11","17",6.366666666666668,8.1066666666666674]
["Vlissingen1118","Vlissingen","11","18",6.126666666666666,8.1066666666666674]
["Vlissingen1119","Vlissingen","11","19",5.5933333333333337,8.16]
["Vlissingen1120","Vlissingen","11","20",6.6533333333333333,7.9133333333333322]
["Vlissingen1121","Vlissingen","11","21",7.1400000000000006,7.7133333333333347]
["Vlissingen1122","Vlissingen","11","22",7.52,8.2533333333333339]
["Vlissingen1123","Vlissingen","11","23",5.8199999999999994,8.3066666666666666]
["Vlissingen1124","Vlissingen","11","24",5.9066666666666654,7.793333333333333]
["Vlissingen1125","Vlissingen","11","25",7.7000000000000011,7.8400000000000007]
["Vlissingen1126","Vlissingen","11","26",6.5666666666666655,7.4]
["Vlissingen1127","Vlissingen","11","27",6.2133333333333329,7.42]
["Vlissingen1128","Vlissingen","11","28",6.52,7.3533333333333344]
["Vlissingen1129","Vlissingen","11","29",6.5533333333333328,6.9266666666666676]
["Vlissingen1130","Vlissingen","11","30",5.8266666666666662,6.5066666666666659]
["Vlissingen1201","Vlissingen","12","01",6.953333333333334,6.6466666666666656]
["Vlissingen1202","Vlissingen","12","02",6.1599999999999993,6.1599999999999993]
["Vlissingen1203","Vlissingen","12","03",6.6133333333333324,5.9533333333333314]
["Vlissingen1204","Vlissingen","12","04",7.7066666666666661,6.2733333333333325]
["Vlissingen1205","Vlissingen","12","05",7.6799999999999988,7.206666666666667]
["Vlissingen1206","Vlissingen","12","06",6.9600000000000017,6.76]
["Vlissingen1207","Vlissingen","12","07",7.3333333333333321,5.6866666666666683]
["Vlissingen1208","Vlissingen","12","08",7.1,5.253333333333333]
["Vlissingen1209","Vlissingen","12","09",6.7666666666666666,5.133333333333332]
["Vlissingen1210","Vlissingen","12","10",6.4999999999999991,4.9866666666666664]
["Vlissingen1211","Vlissingen","12","11",6.5933333333333337,5.4200000000000008]
["Vlissingen1212","Vlissingen","12","12",6.6133333333333324,5.1333333333333337]
["Vlissingen1213","Vlissingen","12","13",7.5000000000000009,4.5999999999999996]
["Vlissingen1214","Vlissingen","12","14",6.8533333333333344,4.3533333333333335]
["Vlissingen1215","Vlissingen","12","15",7.2266666666666683,4.8600000000000003]
["Vlissingen1216","Vlissingen","12","16",6.6799999999999988,4.793333333333333]
["Vlissingen1217","Vlissingen","12","17",6.12,4.22]
["Vlissingen1218","Vlissingen","12","18",5.6800000000000006,4.0666666666666664]
["Vlissingen1219","Vlissingen","12","19",5.8,4.0266666666666673]
["Vlissingen1220","Vlissingen","12","20",6.7799999999999994,4.0933333333333328]
["Vlissingen1221","Vlissingen","12","21",7.0933333333333337,4.5933333333333337]
["Vlissingen1222","Vlissingen","12","22",7.253333333333333,5.4]
["Vlissingen1223","Vlissingen","12","23",7.6466666666666665,5.5466666666666669]
["Vlissingen1224","Vlissingen","12","24",7.6866666666666674,5.626666666666666]
["Vlissingen1225","Vlissingen","12","25",7.22,5.5066666666666659]
["Vlissingen1226","Vlissingen","12","26",6.9000000000000012,4.5733333333333333]
["Vlissingen1227","Vlissingen","12","27",7.6466666666666656,3.8666666666666667]
["Vlissingen1228","Vlissingen","12","28",7.6866666666666674,4.3199999999999994]
["Vlissingen1229","Vlissingen","12","29",7.080000000000001,4.4466666666666663]
["Vlissingen1230","Vlissingen","12","30",7.0733333333333333,4.7266666666666657]
["Vlissingen1231","Vlissingen","12","31",6.7399999999999993,4.746666666666667]

{"sheet":"Subsidie","index":4,"n_rows":12,"n_cols":7,"rows_kept":12,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[null,null,"besparing tussen 0,6 en 1,5 Nm3/j per euro?",null,null,null,{"$f":"IF(F12>=0.6,IF(F12<=1.5,\"ja\",\"nee\"),\"nee\")","v":"ja"}]
[null,null,"prijs ",80,"€/m2","--->",{"$f":"D7*Berekeningen!J10","v":131687.71005685013}]
[null,null,"warmtelek zonder dakisolatie",null,null,268.40863490964659,"kW"]
[null,null,"warmtelek met dakisolatie",null,null,120.18898849659911,"kW"]
[null,null,null,"besparing",null,{"$f":"F8-F9","v":148.21964641304749},"kW"]
[null,null,null,"aardgaseq per jaar:",null,{"$f":"F10*24*365*3.6/31.65","v":147685.77470084882},"Nm3/j"]
[null,null,null,null,null,{"$f":"F11/G7","v":1.1214848723323707}]